## Project Info
Project: | Project Location | Customer Name: | Requested by: | Contact Info: | Date: | Created by: | Estimate Project Cost
Bethany SWD | Bethany, La | Aqua Libre | Raymond Metzler | RMetzler@selectenergy.com | 2023-02-24 | M.Myers | 177329.295

## Cost Summery
Instrumentation
Item | MFG | Description | Unit Price | Quantity | Total Cost
Instrumentation | N/A | Instrument End Devices | 146786 | 1 | 146786
Main Panel | TAS | Main Control Panel | 27031.8417 | 1 | 27031.8417
UPS | TAS | Battery Backup | 3511.4533 | 1 | 3511.4533
SCADA | TAS |  | 0 | 1 | 0
Labor | TAS | Field Installation and Commisioning | 0 | 0 | 0
Other | N/A |  |  |  | 0
0
0
0
|  |  |  | Total | 177329.295

## Item Price List
Instrumentation
Device | MFG | P/N | Description | Unit Price | Margin | Quantity | Cost ea. | Cost | Total Cost
LSH | Magnetrol | 961-2DA1-030 w/ 9A1-A21A-012 | Echotel Model 961 Ultrasonic Level Switch | 625 | 0% | 18 | 625 | 11250 | 11250
LIT | Magnetrol | 706-540A-310 | ECLIPSE 4th Generation Guided Wave Radar Modbus | 2032 | 0% | 7 | 2032 | 14224 | 14224
PIT-1 | Yokogawa | EJA530E-JBS7N-012EL/FU1/D1 | Yokogawa DPharp Digital Direct Mount Gauge Pressure Transmitter 0-290 PSI Min | 732 | 0% | 13 | 732 | 9516 | 9516
PIT-2 | Yokogawa | EJA530E-JDS7N-012EL/FU1/D1 | Yokogawa DPharp Digital Direct Mount Gauge Pressure Transmitter 0-7200 PSI Min | 732 | 0% | 10 | 732 | 7320 | 7320
FIT | Yokogawa | AXG150-CASF2BA1AL212B-2M011/GRL/MC | ADMAG TI Series Magnetic Flowmeter 150mm (6 in.) | 3474 | 0% | 4 | 3474 | 13896 | 13896
MOV | J-Flow Controls | C-2F33FTTTF1LD | 6", Ball Valve, ANSI 150, TRIAC ACTUATOR 7000 MOV | 6470 | 0% | 14 | 6470 | 90580 | 90580
[6 empty] | Total | 14065 | 146786 | 146786
Main Panel
Device | MFG | P/N | Description | Unit Price | Margin | Quantity | Cost ea. | Cost | Total Cost
MCP | Texas Automation Systems | N/A | Main Process Automation Control Panel | 27031.8417 | 0% | 1 | 27031.8417 | 27031.8417 | 27031.8417
|  |  |  | 0 | 0% |  | 0 | 0 | 0
|  |  |  | 0 |  | Total | 27031.8417 | 27031.8417 | 27031.8417
UPS
Device | MFG | P/N | Description | Unit Price | Margin | Quantity | Cost ea. | Cost | Total Cost
UPS | Texas Automation Systems | N/A | UPS/Battery Backup (Main Process Automation Control Panel) | 3511.4533 | 0% | 1 | 3511.4533 | 3511.4533 | 3511.4533
|  |  |  | 0 | 0% |  | 0 | 0 | 0
|  |  |  | 0 |  | Total | 3511.4533 | 3511.4533 | 3511.4533
SCADA
Device | MFG | P/N | Description | Unit Price | Margin | Quantity | Cost ea. | Cost | Total Cost
| Inductive Automation |  | Edge | 0 | 0% | 1 | 0 | 0 | 0
Dev | TAS | N/A | User Product Development | 0 |  |  | 0 | 0 | 0
|  |  |  | 0 | 0% |  | 0 | 0 | 0
|  |  |  | 0 |  | Total | 0 | 0 | 0
Labor
Device | MFG | P/N | Description | Unit Price | Margin | Quantity | Cost ea. | Cost | Total Cost
|  |  |  | 0 | 0% | 1 | 0 | 0 | 0
|  |  |  | 0 | 0% |  | 0 | 0 | 0
|  |  |  | 0 |  | Total | 0 | 0 | 0
Other
Device | MFG | P/N | Description | Unit Price | Margin | Quantity | Cost ea. | Cost | Total Cost
|  |  |  | 0 | 0% | 0 | 0 | 0 | 0
|  |  |  | 0 | 0 |  | 0 | 0 | 0
|  |  |  | 0 | 0% |  | 0 | 0 | 0
|  |  |  | 0 |  | Total | 0 | 0 | 0
Bethany SWD
Cost Estimate and I/O List

## IO Summery
id | AI | AO | DI | DO | MB | Device
PIT | 23 |  |  |  |  | PSI Indicator
LSH |  |  | 18 |  |  | Level High Switch
LIT |  |  |  |  | 7 | Level Indicator
FIT |  |  |  |  | 4 | Flow Indicator
MOV |  |  | 13 | 14 |  | Motor Operated Valve
OLS |  |  | 6 |  |  | Oil Level SW
VS |  |  | 6 |  |  | Vibration Switch
LLS |  |  | 6 |  |  | Lube Level Switch
SW |  |  | 5 | 5 |  | Hand Switch/Button
PMP Panel |  |  | 5 | 7 |  | Pump Panel
SL |  |  |  | 1 |  | Signal Light
HRN |  |  |  | 1 |  | Horn
ES |  |  | 4 |  |  | E-Stop
DRV |  |  |  |  | 6
Total AI | 23
Total AO | 0
Total DI | 63
Total DO | 28
Total MB | 17

## Master List (hidden)
Unlisted | Tag | PID | Equipment | Signal Type | AI | AI Signal Use | AO | AO Signal Use | DI | DI Signal Use | DO | DO Signal Use | MB | MB Signal Use | HMI Action/Indicated | PLC / HMI Function | MFG | P/N | Description | Notes
| P-100 | PID-1000 | Offload Pump Panel | DO | 0 | N/A | 0 | N/A | 0 | Transaction Start Switch | 1 | Transaction Stop Switch | 0 | N/A | Yes | Start Transaction Switch |  |  |  | Switch Located at Trucking Lane
| P-100 cont. | PID-1000 | Offload Pump Panel |  | 0 | N/A | 0 |  | 0 | Transaction Stop Switch | 1
| P-100 cont. | PID-1000 | Offload Pump Panel | DI | 0 | N/A | 0 | N/A | 1 | Offload Pump Status | 0 | N/A | 0 | N/A | Yes | Run Status, Fail to Start Alarm |  |  |  | REQUIRED--aux contact/status (m.myers)
| P-101 | PID-1000 | Offload Pump Panel | DO | 0 | N/A | 0 | N/A | 0 | Transaction Start Switch | 1 | Transaction Stop Switch | 0 | N/A | Yes | Auto & Manual Control |  |  |  | REQUIRED--aux contact/status (m.myers)
| P-101 cont. | PID-1000 | Offload Pump Panel |  | 0 | N/A | 0 | N/A | 0 | Transaction Stop Switch | 1
| P-101 cont. | PID-1000 | Offload Pump Panel | DI | 0 | N/A | 0 | N/A | 1 | Offload Pump Status | 0 | N/A | 0 | N/A | Yes | Run Status, Fail to Start Alarm |  |  |  | REQUIRED--aux contact/status (m.myers)
| P-102 | PID-1000 |  | DO | 0 |  |  | N/A | 0 | Transaction Start Switch | 1 | Transaction Stop Switch | 0 | N/A | Yes | Auto & Manual Control |  |  |  | REQUIRED--aux contact/status (m.myers)
| P-102 cont. | PID-1000 | Offload Pump Panel |  | 0 | N/A | 0 | N/A | 0 | Transaction Start Switch | 1
| P-102 cont. | PID-1000 | Offload Pump Panel | DI | 0 | N/A | 0 | N/A | 1 | Offload Pump Status | 0 | N/A | 0 | N/A | Yes | Run Status, Fail to Start Alarm |  |  |  | REQUIRED--aux contact/status (m.myers)
| P-300 | PID-1000 | Transfer Pump Panel Switch | DO | 0 | N/A | 0 | N/A | 1 | Transfer Pump Start | 1 | Transfer Pump Stop | 0 | N/A |  | Auto & Manual Control |  |  |  | REQUIRED--aux contact/status (m.myers)
| P-300 cont. | PID-1000 | Transfer Pump Panel Switch | DI | 0 | N/A | 0 | N/A | 1 | Transfer Pump Status | 0 | N/A | 0 | N/A |  | Run Status, Fail to Start Alarm |  |  |  | REQUIRED--aux contact/status (m.myers)
| P-301 | PID-1000 | Transfer Pump Panel Switch | DO | 0 | N/A | 0 | N/A | 1 | Transfer Pump Start | 1 | Transfer Pump Stop | 0 | N/A |  | Auto & Manual Control |  |  |  | REQUIRED--aux contact/status (m.myers)
| P-301 cont. | PID-1000 | Transfer Pump Panel Switch | DI | 0 | N/A | 0 | N/A | 1 | Transfer Pump Status | 0 | N/A | 0 | N/A |  | Run Status, Fail to Start Alarm |  |  |  | REQUIRED--aux contact/status (m.myers)
| P-600 | PID-1001 | Well #1 Injection Charge Pump Panel | DI | 0 | N/A | 0 | N/A | 0 | Start Command to motor starter | 1 | Start Command to motor starter | 0 | N/A |  | Auto & Manual Control |  |  |  | HOA installed on drive & pump Panel(RUN/STOP--status, fault, speed, amps,hz)
| P-600 cont. | PID-1001 | Well #1 Injection Charge Pump Panel | DI | 0 | N/A | 0 | N/A | 1 | Well #1 Injection Charge Pump Panel Status | 0 | N/A | 0 | N/A |  | Run Status, Fail to Start Alarm |  |  |  | RUN/STOP--status, fault, speed, amps,hz
| P-601 | PID-1001 | Well #1 Injection Pump #1 Drive | MB | 0 | N/A | 0 | N/A | 0 | N/A | 0 | N/A | 1 | Start Command to Drive |  | Auto & Manual Control |  |  |  | RUN/STOP--status, fault, speed, amps,hz
| P-601 cont. | PID-1001 | Well #1 Injection Pump #1 Drive | MB | 0 | N/A | 0 | N/A | 1 | Well #1 Injection Pump #1 Drive Status | 0 | N/A | 1 | Run feedback from Drive |  | Run Status, Fail to Start Alarm |  |  |  | RUN/STOP--status, fault, speed, amps,hz
| P-602 | PID-1001 | Well #1 Injection Pump #2 Drive | MB | 0 | N/A | 0 | N/A | 0 | N/A | 0 | N/A | 1 | Start Command to motor starter |  | Auto & Manual Control |  |  |  | RUN/STOP--status, fault, speed, amps,hz
| P-602 cont. | PID-1001 | Well #1 Injection Pump #2 Drive | MB | 0 | N/A | 0 | N/A | 1 | Well #1 Injection Pump #2 Drive Status | 0 | N/A | 1 | Run feedback from motor starter |  | Run Status, Fail to Start Alarm |  |  |  | RUN/STOP--status, fault, speed, amps,hz
| P-700 | PID-1001 | Well #2 Injection Charge Pump #1 | DI | 0 | N/A | 0 | N/A | 0 | N/A | 1 | Start Command to motor starter | 0 |  |  | Auto & Manual Control |  |  |  | RUN/STOP--status, fault, speed, amps,hz
| P-700 cont. | PID-1001 | Well #2 Injection Charge Pump #1 | DI | 0 | N/A | 0 | N/A | 1 | Well #2 Injection Charge Pump #1 Status | 0 | N/A | 0 | Run feedback from motor starter |  | Run Status, Fail to Start Alarm |  |  |  | RUN/STOP--status, fault, speed, amps,hz
| P-701 | PID-1001 | Well #2 Injection Pump #1 | MB | 0 | N/A | 0 | N/A | 0 | N/A | 0 | Start Command to motor starter | 1 | Start Command to motor starter |  | Auto & Manual Control |  |  |  | RUN/STOP--status, fault, speed, amps,hz
| P-701 cont. | PID-1001 | Well #2 Injection Pump #1 | MB | 0 | N/A | 0 | N/A | 0 | Well #2 Injection Pump #1 Status | 0 | N/A | 1 | Run feedback from motor starter |  | Run Status, Fail to Start Alarm |  |  |  | RUN/STOP--status, fault, speed, amps,hz
| P-702 | PID-1001 | Well #2 Injection Charge Pump #2 | MB | 0 | N/A | 0 | N/A | 0 | N/A | 1 | Start Command to motor starter | 0 | Start Command to motor starter |  | Auto & Manual Control |  |  |  | RUN/STOP--status, fault, speed, amps,hz
| P-702 cont. | PID-1001 | Well #2 Injection Charge Pump #2 | MB | 0 | N/A | 0 | N/A | 1 | Well #2 Injection Charge Pump #2 Status | 0 | N/A | 0 | Run feedback from motor starter |  | Run Status, Fail to Start Alarm |  |  |  | RUN/STOP--status, fault, speed, amps,hz
| P-703 | PID-1001 | Well #2 Injection Pump #2 | MB | 0 | N/A | 0 | N/A | 0 | N/A | 0 | Start Command to motor starter | 1 | Start Command to motor starter |  | Auto & Manual Control |  |  |  | RUN/STOP--status, fault, speed, amps,hz
| P-703 cont. | PID-1001 | Well #2 Injection Pump #2 | MB | 0 | N/A | 0 | N/A | 0 | Well #2 Injection Pump #2 Status | 0 | N/A | 1 | Run feedback from motor starter |  | Run Status, Fail to Start Alarm |  |  |  | RUN/STOP--status, fault, speed, amps,hz
| P-704 | PID-1001 | Well #2 Injection Charge Pump #3 | MB | 0 | N/A | 0 | N/A | 0 | N/A | 1 | Start Command to motor starter | 0 | Start Command to motor starter |  | Auto & Manual Control |  |  |  | RUN/STOP--status, fault, speed, amps,hz
| P-704 cont. | PID-1001 | Well #2 Injection Charge Pump #3 | MB | 0 | N/A | 0 | N/A | 1 | Well #2 Injection Charge Pump #3 Status | 0 | N/A | 0 | Run feedback from motor starter |  | Run Status, Fail to Start Alarm |  |  |  | RUN/STOP--status, fault, speed, amps,hz
| P-705 | PID-1001 | Well #2 Injection Pump #3 | MB | 0 | N/A | 0 | N/A | 0 | N/A | 0 | Start Command to motor starter | 1 | Start Command to motor starter |  | Auto & Manual Control |  |  |  | RUN/STOP--status, fault, speed, amps,hz
| P-705 cont. | PID-1001 | Well #2 Injection Pump #3 | MB | 0 | N/A | 0 | N/A | 0 | Well #2 Injection Pump #3 Status | 0 | N/A | 1 | Run feedback from motor starter |  | Run Status, Fail to Start Alarm |  |  |  | RUN/STOP--status, fault, speed, amps,hz
| P-706 | PID-1001 | Well #2 Injection Charge Pump #4 | MB | 0 | N/A | 0 | N/A | 0 | N/A | 1 | Start Command to motor starter | 0 | Start Command to motor starter |  | Auto & Manual Control |  |  |  | RUN/STOP--status, fault, speed, amps,hz
| P-706 cont. | PID-1001 | Well #2 Injection Charge Pump #4 | MB | 0 | N/A | 0 | N/A | 1 | Well #2 Injection Charge Pump #4 Status | 0 | N/A | 0 | Run feedback from motor starter |  | Run Status, Fail to Start Alarm |  |  |  | RUN/STOP--status, fault, speed, amps,hz
| P-707 | PID-1001 | Well #2 Injection Pump #4 | MB | 0 | N/A | 0 | N/A | 0 | N/A | 0 | Start Command to motor starter | 1 | Start Command to motor starter |  | Auto & Manual Control |  |  |  | RUN/STOP--status, fault, speed, amps,hz
| P-707 cont. | PID-1001 | Well #2 Injection Pump #4 | MB | 0 | N/A | 0 | N/A | 0 | Well #2 Injection Pump #4 Status | 0 | N/A | 1 | Run feedback from motor starter |  | Run Status, Fail to Start Alarm |  |  |  | RUN/STOP--status, fault, speed, amps,hz
[17 empty] | Total Required | N/A
| P-103 | PID-1000 | Drain Sump Pump | N/A |  | N/A | 0 |  |  |  |  | N/A |  | No control needed. |  | None
| P-105 | PID-1000 | Containment Sump Pump | N/A |  | N/A | 0 | [6 empty] | No control needed. |  | None
LSH | Total Required | 18
| LSH-001 | PID-1000 | Buffer Tank TK-001 | DI | 0 | N/A | 0 | N/A | 1 | High Level | 0 | N/A | 0 | N/A |  | Status and High Level Alarm | Magnetrol | 961-2DA1-030 w/ 9A1-A21A-012 | Echotel Model 961 Ultrasonic Level Switch | Is this a float or tuning fork style that need separate 24VDC power?
| LSH-002 | PID-1000 | Buffer Tank TK-002 | DI | 0 | N/A | 0 | N/A | 1 | High Level | 0 | N/A | 0 | N/A |  | Status and High Level Alarm | Magnetrol | 961-2DA1-030 w/ 9A1-A21A-012 | Echotel Model 961 Ultrasonic Level Switch | Is this a float or tuning fork style that need separate 24VDC power?
| LSH-003 | PID-1000 | Buffer Tank TK-003 | DI | 0 | N/A | 0 | N/A | 1 | High Level | 0 | N/A | 0 | N/A |  | Status and High Level Alarm | Magnetrol | 961-2DA1-030 w/ 9A1-A21A-012 | Echotel Model 961 Ultrasonic Level Switch | Is this a float or tuning fork style that need separate 24VDC power?
| LSH-004 | PID-1000 | Buffer Tank TK-004 | DI | 0 | N/A | 0 | N/A | 1 | High Level | 0 | N/A | 0 | N/A |  | Status and High Level Alarm | Magnetrol | 961-2DA1-030 w/ 9A1-A21A-012 | Echotel Model 961 Ultrasonic Level Switch | Is this a float or tuning fork style that need separate 24VDC power?
| LSH-005 | PID-1000 | Buffer Tank TK-005 | DI | 0 | N/A | 0 | N/A | 1 | High Level | 0 | N/A | 0 | N/A |  | Status and High Level Alarm | Magnetrol | 961-2DA1-030 w/ 9A1-A21A-012 | Echotel Model 961 Ultrasonic Level Switch | Is this a float or tuning fork style that need separate 24VDC power?
| LSH-006 | PID-1000 | Buffer Tank TK-006 | DI | 0 | N/A | 0 | N/A | 1 | High Level | 0 | N/A | 0 | N/A |  | Status and High Level Alarm | Magnetrol | 961-2DA1-030 w/ 9A1-A21A-012 | Echotel Model 961 Ultrasonic Level Switch | Is this a float or tuning fork style that need separate 24VDC power?
| LSH-007 | PID-1000 | Buffer Tank TK-007 | DI | 0 | N/A | 0 | N/A | 1 | High Level | 0 | N/A | 0 | N/A |  | Status and High Level Alarm | Magnetrol | 961-2DA1-030 w/ 9A1-A21A-012 | Echotel Model 961 Ultrasonic Level Switch | Is this a float or tuning fork style that need separate 24VDC power?
| LSH-008 | PID-1000 | Buffer Tank TK-008 | DI | 0 | N/A | 0 | N/A | 1 | High Level | 0 | N/A | 0 | N/A |  | Status and High Level Alarm | Magnetrol | 961-2DA1-030 w/ 9A1-A21A-012 | Echotel Model 961 Ultrasonic Level Switch | Is this a float or tuning fork style that need separate 24VDC power?
| LSH-009 | PID-1001 | Clean Tank TK-009 | DI | 0 | N/A | 0 | N/A | 1 | High Level | 0 | N/A | 0 | N/A |  | Status and High Level Alarm | Magnetrol | 961-2DA1-030 w/ 9A1-A21A-012 | Echotel Model 961 Ultrasonic Level Switch | Is this a float or tuning fork style that need separate 24VDC power?
| LSH-010 | PID-1001 | Clean Tank TK-010 | DI | 0 | N/A | 0 | N/A | 1 | High Level | 0 | N/A | 0 | N/A |  | Status and High Level Alarm | Magnetrol | 961-2DA1-030 w/ 9A1-A21A-012 | Echotel Model 961 Ultrasonic Level Switch | Is this a float or tuning fork style that need separate 24VDC power?
| LSH-011 | PID-1001 | Clean Tank TK-011 (Existing) | DI | 0 | N/A | 0 | N/A | 1 | High Level | 0 | N/A | 0 | N/A |  | Status and High Level Alarm | Magnetrol | 961-2DA1-030 w/ 9A1-A21A-012 | Echotel Model 961 Ultrasonic Level Switch | Is this a float or tuning fork style that need separate 24VDC power?
| LSH-012 | PID-1001 | Clean Tank TK-012 (Existing) | DI | 0 | N/A | 0 | N/A | 1 | High Level | 0 | N/A | 0 | N/A |  | Status and High Level Alarm | Magnetrol | 961-2DA1-030 w/ 9A1-A21A-012 | Echotel Model 961 Ultrasonic Level Switch | Is this a float or tuning fork style that need separate 24VDC power?
| LSH-013 | PID-1001 | Clean Tank TK-013 (Existing) | DI | 0 | N/A | 0 | N/A | 1 | High Level | 0 | N/A | 0 | N/A |  | Status and High Level Alarm | Magnetrol | 961-2DA1-030 w/ 9A1-A21A-012 | Echotel Model 961 Ultrasonic Level Switch | Is this a float or tuning fork style that need separate 24VDC power?
| LSH-014 | PID-1001 | Clean Tank TK-014 (Existing) | DI | 0 | N/A | 0 | N/A | 1 | High Level | 0 | N/A | 0 | N/A |  | Status and High Level Alarm | Magnetrol | 961-2DA1-030 w/ 9A1-A21A-012 | Echotel Model 961 Ultrasonic Level Switch | Is this a float or tuning fork style that need separate 24VDC power?
| LSH-020 | PID-1000 | Oil Tank TK-020 | DI | 0 | N/A | 0 | N/A | 1 | High Level | 0 | N/A | 0 | N/A |  | Status and High Level Alarm | Magnetrol | 961-2DA1-030 w/ 9A1-A21A-012 | Echotel Model 961 Ultrasonic Level Switch | Is this a float or tuning fork style that need separate 24VDC power?
| LSH-021 | PID-1000 | Oil Tank TK-021 | DI | 0 | N/A | 0 | N/A | 1 | High Level | 0 | N/A | 0 | N/A |  | Status and High Level Alarm | Magnetrol | 961-2DA1-030 w/ 9A1-A21A-012 | Echotel Model 961 Ultrasonic Level Switch | Is this a float or tuning fork style that need separate 24VDC power?
| LSH-030 | PID-1000 | Gun Barrel TK-030 | DI | 0 | N/A | 0 | N/A | 1 | High Level | 0 | N/A | 0 | N/A |  | Status and High Level Alarm | Magnetrol | 961-2DA1-030 w/ 9A1-A21A-012 | Echotel Model 961 Ultrasonic Level Switch | Is this a float or tuning fork style that need separate 24VDC power?
| LSH-031 | PID-1000 | Gun Barrel TK-031 | DI | 0 | N/A | 0 | N/A | 1 | High Level | 0 | N/A | 0 | N/A |  | Status and High Level Alarm | Magnetrol | 961-2DA1-030 w/ 9A1-A21A-012 | Echotel Model 961 Ultrasonic Level Switch | Is this a float or tuning fork style that need separate 24VDC power?
[17 empty] | Total Required | 18
LIT | Total Required | 7
| LIT-007 | PID-1000 | Buffer Tank TK-007 | AI | 0 | Tank Level | 0 | N/A | 0 | N/A | 0 | N/A | 1 | Level |  | Tank Level in %, High Level Alarm, Low Level Alarm, Enable for Pumps | Magnetrol | 706-540A-310 | ECLIPSE 4th Generation Guided Wave Radar
| LIT-008 | PID-1000 | Buffer Tank TK-008 | AI | 0 | Tank Level | 0 | N/A | 0 | N/A | 0 | N/A | 1 | Level |  | Tank Level in %, High Level Alarm, Low Level Alarm, Enable for Pumps | Magnetrol | 706-540A-310
| LIT-021 | PID-1000 | Oil Tank TK-021 | AI | 0 | Tank Level | 0 | N/A | 0 | N/A | 0 | N/A | 1 | Level |  | Tank Level in %, High Level Alarm, Low Level Alarm, Enable for Pumps | Magnetrol | 706-540A-310
| LIT-030 | PID-1000 | Gun Barrel TK-030 | AI | 0 | Tank Level | 0 | N/A | 0 | N/A | 0 | N/A | 1 | Level |  | Tank Level in %, High Level Alarm, Low Level Alarm, Enable for Pumps | Magnetrol | 706-540A-310
| LIT-031 | PID-1000 | Gun Barrel TK-031 | AI | 0 | Tank Level | 0 | N/A | 0 | N/A | 0 | N/A | 1 | Level |  | Tank Level in %, High Level Alarm, Low Level Alarm, Enable for Pumps | Magnetrol | 706-540A-310
| LIT-013 | PID-1001 | Clean Tank TK-013 (Existing) | AI | 0 | Tank Level | 0 | N/A | 0 | N/A | 0 | N/A | 1 | Level |  | Tank Level in %, High Level Alarm, Low Level Alarm, Enable for Pumps | Magnetrol | 706-540A-310
| LIT-014 | PID-1001 | Clean Tank TK-014 (Existing) | AI | 0 | Tank Level | 0 | N/A | 0 | N/A | 0 | N/A | 1 | Level |  | Tank Level in %, High Level Alarm, Low Level Alarm, Enable for Pumps | Magnetrol | 706-540A-310
[17 empty] | Total Required | 7
PIT | Total Required | 23
| PIT-601 | PID-1001 | Well #1 Injection Run Filter #1 (F-600 prefilter) In uses as DP | AI | 1 | Pressure in PSIG, High Level Alarm, Low Level Alarm, | 0 | N/A | 0 | N/A | 0 | N/A | 0 | N/A |  | Pressure in PSIG, High Level Alarm, Low Level Alarm, | Magnetrol | EJA530E-JBS7N-012EL/FU1/D1 | Yokogawa DPharp Digital Direct Mount Gauge Pressure Transmitter 0-290 PSI Min | is this changing to a DPIT instead of 2 PITs
| PIT-602 | PID-1001 | Well #1 Injection Run Filter #1 (F-600 Post Filter) In uses as DP | AI | 1 | Pressure in PSIG, High Level Alarm, Low Level Alarm, | 0 | N/A | 0 | N/A | 0 | N/A | 0 | N/A |  | Pressure in PSIG, High Level Alarm, Low Level Alarm, | Magnetrol | EJA530E-JBS7N-012EL/FU1/D1 | Yokogawa DPharp Digital Direct Mount Gauge Pressure Transmitter 0-290 PSI Min | is this changing to a DPIT instead of 2 PITs
| PIT-607 | PID-1001 | Well #1 Injection Run Filter #2 (F-601 prefilter) In uses as DP | AI | 1 | Pressure in PSIG, High Level Alarm, Low Level Alarm, | 0 | N/A | 0 | N/A | 0 | N/A | 0 | N/A |  | Pressure in PSIG, High Level Alarm, Low Level Alarm, | Magnetrol | EJA530E-JBS7N-012EL/FU1/D1 | Yokogawa DPharp Digital Direct Mount Gauge Pressure Transmitter 0-290 PSI Min | is this changing to a DPIT instead of 2 PITs
| PIT-608 | PID-1001 | Well #1 Injection Run Filter #2 (F-601 postfilter) In uses as DP | AI | 1 | Pressure in PSIG, High Level Alarm, Low Level Alarm, | 0 | N/A | 0 | N/A | 0 | N/A | 0 | N/A |  | Pressure in PSIG, High Level Alarm, Low Level Alarm, | Magnetrol | EJA530E-JBS7N-012EL/FU1/D1 | Yokogawa DPharp Digital Direct Mount Gauge Pressure Transmitter 0-290 PSI Min | is this changing to a DPIT instead of 2 PITs
| PIT-621 | PID-1001 | Well #1 Injection Run Suction Header (Wellhead #1 Injection pump header) | AI | 1 | Pressure in PSIG, High Level Alarm, Low Level Alarm, | 0 | N/A | 0 | N/A | 0 | N/A | 0 | N/A |  | Pressure in PSIG, High Level Alarm, Low Level Alarm, | Magnetrol | EJA530E-JBS7N-012EL/FU1/D1 | Yokogawa DPharp Digital Direct Mount Gauge Pressure Transmitter 0-290 PSI Min
| PIT-619 | PID-1001 | Well #1 Injection Run 1 (P-601 Discharge PSI) | AI | 1 | Pressure in PSIG, High Level Alarm, Low Level Alarm, | 0 | N/A | 0 | N/A | 0 | N/A | 0 | N/A |  | Pressure in PSIG, High Level Alarm, Low Level Alarm, | Magnetrol | EJA530E-JDS7N-012EL/FU1/D1 | Yokogawa DPharp Digital Direct Mount Gauge Pressure Transmitter 0-7200 PSI Min | is this changing to a DPIT instead of 2 PITs
| PIT-629 | PID-1001 | Well #1 Injection Run 2 (P-602 Discharge PSI) | AI | 1 | Pressure in PSIG, High Level Alarm, Low Level Alarm, | 0 | N/A | 0 | N/A | 0 | N/A | 0 | N/A |  | Pressure in PSIG, High Level Alarm, Low Level Alarm, | Magnetrol | EJA530E-JBS7N-012EL/FU1/D1 | Yokogawa DPharp Digital Direct Mount Gauge Pressure Transmitter 0-7200 PSI Min | is this changing to a DPIT instead of 2 PITs
| PIT-633 | PID-1001 | Well #1 Injection to well (Injection PSI) | AI | 1 | Pressure in PSIG, High Level Alarm, Low Level Alarm, | 0 | N/A | 0 | N/A | 0 | N/A | 0 | N/A |  | Pressure in PSIG, High Level Alarm, Low Level Alarm, | Magnetrol | EJA530E-JDS7N-012EL/FU1/D1 | Yokogawa DPharp Digital Direct Mount Gauge Pressure Transmitter 0-7200 PSI Min
| PIT-634 | PID-1001 | Well #1 Injection to well ( Anulus) | AI | 1 | Pressure in PSIG, High Level Alarm, Low Level Alarm, | 0 | N/A | 0 | N/A | 0 | N/A | 0 | N/A |  | Pressure in PSIG, High Level Alarm, Low Level Alarm, | Magnetrol | EJA530E-JDS7N-012EL/FU1/D1 | Yokogawa DPharp Digital Direct Mount Gauge Pressure Transmitter 0-7200 PSI Min
| PIT-701 | PID-1001 | Well #2 Injection Run 1 Filter (F-701 prefilter) In uses as DP | AI | 1 | Pressure in PSIG, High Level Alarm, Low Level Alarm, | 0 | N/A | 0 | N/A | 0 | N/A | 0 | N/A |  | Pressure in PSIG, High Level Alarm, Low Level Alarm, | Magnetrol | EJA530E-JBS7N-012EL/FU1/D1 | Yokogawa DPharp Digital Direct Mount Gauge Pressure Transmitter 0-290 PSI Min | is this changing to a DPIT instead of 2 PITs
| PIT-703 | PID-1001 | Well #2 Injection Run 1 Filter (F-701 postfilter) In uses as DP | AI | 1 | Pressure in PSIG, High Level Alarm, Low Level Alarm, | 0 | N/A | 0 | N/A | 0 | N/A | 0 | N/A |  | Pressure in PSIG, High Level Alarm, Low Level Alarm, | Magnetrol | EJA530E-JBS7N-012EL/FU1/D1 | Yokogawa DPharp Digital Direct Mount Gauge Pressure Transmitter 0-290 PSI Min | is this changing to a DPIT instead of 2 PITs
| PIT-710 | PID-1001 | Well #2 Injection Run 1 (P-701 Discharge PSI) | AI | 1 | Pressure in PSIG, High Level Alarm, Low Level Alarm, | 0 | N/A | 0 | N/A | 0 | N/A | 0 | N/A |  | Pressure in PSIG, High Level Alarm, Low Level Alarm, | Magnetrol | EJA530E-JDS7N-012EL/FU1/D1 | Yokogawa DPharp Digital Direct Mount Gauge Pressure Transmitter 0-7200 PSI Min
| PIT-713 | PID-1001 | Well #2 Injection Run 2 Filter (F-702 prefilter) In uses as DP | AI | 1 | Pressure in PSIG, High Level Alarm, Low Level Alarm, | 0 | N/A | 0 | N/A | 0 | N/A | 0 | N/A |  | Pressure in PSIG, High Level Alarm, Low Level Alarm, | Magnetrol | EJA530E-JBS7N-012EL/FU1/D1 | Yokogawa DPharp Digital Direct Mount Gauge Pressure Transmitter 0-290 PSI Min | is this changing to a DPIT instead of 2 PITs
| PIT-715 | PID-1001 | Well #2 Injection Run 2 Filter (F-702 postfilter) In uses as DP | AI | 1 | Pressure in PSIG, High Level Alarm, Low Level Alarm, | 0 | N/A | 0 | N/A | 0 | N/A | 0 | N/A |  | Pressure in PSIG, High Level Alarm, Low Level Alarm, | Magnetrol | EJA530E-JBS7N-012EL/FU1/D1 | Yokogawa DPharp Digital Direct Mount Gauge Pressure Transmitter 0-290 PSI Min | is this changing to a DPIT instead of 2 PITs
| PIT-722 | PID-1001 | Well #2 Injection Run 2 (P-703 Discharge PSI) | AI | 1 | Pressure in PSIG, High Level Alarm, Low Level Alarm, | 0 | N/A | 0 | N/A | 0 | N/A | 0 | N/A |  | Pressure in PSIG, High Level Alarm, Low Level Alarm, | Magnetrol | EJA530E-JDS7N-012EL/FU1/D1 | Yokogawa DPharp Digital Direct Mount Gauge Pressure Transmitter 0-7200 PSI Min
| PIT-725 | PID-1001 | Well #2 Injection Run 3 Filter (F-704 prefilter) In uses as DP | AI | 1 | Pressure in PSIG, High Level Alarm, Low Level Alarm, | 0 | N/A | 0 | N/A | 0 | N/A | 0 | N/A |  | Pressure in PSIG, High Level Alarm, Low Level Alarm, | Magnetrol | EJA530E-JBS7N-012EL/FU1/D1 | Yokogawa DPharp Digital Direct Mount Gauge Pressure Transmitter 0-290 PSI Min | is this changing to a DPIT instead of 2 PITs
| PIT-727 | PID-1001 | Well #2 Injection Run 3 Filter (F-704 postfilter) In uses as DP | AI | 1 | Pressure in PSIG, High Level Alarm, Low Level Alarm, | 0 | N/A | 0 | N/A | 0 | N/A | 0 | N/A |  | Pressure in PSIG, High Level Alarm, Low Level Alarm, | Magnetrol | EJA530E-JBS7N-012EL/FU1/D1 | Yokogawa DPharp Digital Direct Mount Gauge Pressure Transmitter 0-290 PSI Min | is this changing to a DPIT instead of 2 PITs
| PIT-734 | PID-1001 | Well #2 Injection Run 3 (P-705 Discharge PSI) | AI | 1 | Pressure in PSIG, High Level Alarm, Low Level Alarm, | 0 | N/A | 0 | N/A | 0 | N/A | 0 | N/A |  | Pressure in PSIG, High Level Alarm, Low Level Alarm, | Magnetrol | EJA530E-JDS7N-012EL/FU1/D1 | Yokogawa DPharp Digital Direct Mount Gauge Pressure Transmitter 0-7200 PSI Min
| PIT-737 | PID-1001 | Well #2 Injection Run 4 Filter (F-706 prefilter) In uses as DP | AI | 1 | Pressure in PSIG, High Level Alarm, Low Level Alarm, | 0 | N/A | 0 | N/A | 0 | N/A | 0 | N/A |  | Pressure in PSIG, High Level Alarm, Low Level Alarm, | Magnetrol | EJA530E-JBS7N-012EL/FU1/D1 | Yokogawa DPharp Digital Direct Mount Gauge Pressure Transmitter 0-290 PSI Min | is this changing to a DPIT instead of 2 PITs
| PIT-739 | PID-1001 | Well #2 Injection Run 4 Filter (F-706 postfilter) In uses as DP | AI | 1 | Pressure in PSIG, High Level Alarm, Low Level Alarm, | 0 | N/A | 0 | N/A | 0 | N/A | 0 | N/A |  | Pressure in PSIG, High Level Alarm, Low Level Alarm, | Magnetrol | EJA530E-JBS7N-012EL/FU1/D1 | Yokogawa DPharp Digital Direct Mount Gauge Pressure Transmitter 0-290 PSI Min | is this changing to a DPIT instead of 2 PITs
| PIT-746 | PID-1001 | Well #2 Injection Run 4 Filter (P-706 Discharge PSI) | AI | 1 | Pressure in PSIG, High Level Alarm, Low Level Alarm, | 0 | N/A | 0 | N/A | 0 | N/A | 0 | N/A |  | Pressure in PSIG, High Level Alarm, Low Level Alarm, | Magnetrol | EJA530E-JDS7N-012EL/FU1/D1 | Yokogawa DPharp Digital Direct Mount Gauge Pressure Transmitter 0-7200 PSI Min
| PIT-750 | PID-1001 | Well #2 Injection to well (Injection PSI) | AI | 1 | Pressure in PSIG, High Level Alarm, Low Level Alarm, | 0 | N/A | 0 | N/A | 0 | N/A | 0 | N/A |  | Pressure in PSIG, High Level Alarm, Low Level Alarm, | Magnetrol | EJA530E-JDS7N-012EL/FU1/D1 | Yokogawa DPharp Digital Direct Mount Gauge Pressure Transmitter 0-7200 PSI Min
| PIT-751 | PID-1001 | Well #2 Injection to well (Anulus PS) | AI | 1 | Pressure in PSIG, High Level Alarm, Low Level Alarm, | 0 | N/A | 0 | N/A | 0 | N/A | 0 | N/A |  | Pressure in PSIG, High Level Alarm, Low Level Alarm, | Magnetrol | EJA530E-JDS7N-012EL/FU1/D1 | Yokogawa DPharp Digital Direct Mount Gauge Pressure Transmitter 0-7200 PSI Min
[17 empty] | Total Required | 23
FIT | Total Required | 4
| FIT-700 | PID-1000 | Comstock Line | AI | 1 | Pressure in PSIG, High Level Alarm, Low Level Alarm, | 0 | N/A | 0 | N/A | 0 | N/A | 0 | N/A |  | Flow in GPM, Daily Total, Historical Totals |  |  |  | what type of meter this
| FIT-600 | PID-1001 | Well #1 Injection Run Suction Header | AI | 1 | Pressure in PSIG, High Level Alarm, Low Level Alarm, | 0 | N/A | 0 | N/A | 0 | N/A | 0 | N/A |  | Flow in GPM, Daily Total, Historical Totals |  |  |  | what type of meter this
| FIT-601 | PID-1001 | Well #1 Injection to well | AI | 1 | Pressure in PSIG, High Level Alarm, Low Level Alarm, | 0 | N/A | 0 | N/A | 0 | N/A | 0 | N/A |  | Flow in GPM, Daily Total, Historical Totals |  |  |  | what type of meter this
| FIT-700 | PID-1001 | Well #2 Injection to well | AI | 1 | Pressure in PSIG, High Level Alarm, Low Level Alarm, | 0 | N/A | 0 | N/A | 0 | N/A | 0 | N/A |  | Flow in GPM, Daily Total, Historical Totals |  |  |  | what type of meter this
[17 empty] | Total Required | 4
P-601
* | P-601 cont. | PID-1001 | Well #1 Injection Pump #1 |  | 0 | N/A | 0 | N/A | 1 | Injection pump Vibration Switch | 0 | N/A | 0 | N/A | [5 empty] | Murphy VS1 Vibration Switch preinstalled on exsisting injection pump
* | P-601 cont. | PID-1001 | Well #1 Injection Pump #1 |  | 0 | N/A | 0 | N/A | 1 | Injection pump Oillevel Switch | 0 | N/A | 0 | N/A | [5 empty] | Murphy VS1 Vibration Switch preinstalled on exsisting injection pump
* | P-601 cont. | PID-1001 | Well #1 Injection Pump #1 |  | 0 | N/A | 0 | N/A | 1 | Injection pump Lube Box Level Switch | 0 | N/A | 0 | N/A | [5 empty] | Murphy VS1 Vibration Switch preinstalled on exsisting injection pump
P-602
* | P-602 cont. | PID-1001 | Well #1 Injection Pump #2 |  | 0 | N/A | 0 | N/A | 1 | Injection pump Vibration Switch | 0 | N/A | 0 | N/A | [5 empty] | Murphy VS1 Vibration Switch preinstalled on exsisting injection pump
* | P-602 cont. | PID-1001 | Well #1 Injection Pump #2 |  | 0 | N/A | 0 | N/A | 1 | Injection pump Oillevel Switch | 0 | N/A | 0 | N/A | [5 empty] | Murphy VS1 Vibration Switch preinstalled on exsisting injection pump
* | P-602 cont. | PID-1001 | Well #1 Injection Pump #2 |  | 0 | N/A | 0 | N/A | 1 | Injection pump Lube Box Level Switch | 0 | N/A | 0 | N/A | [5 empty] | Murphy VS1 Vibration Switch preinstalled on exsisting injection pump
P-701
* | P-701 cont. | PID-1001 | Well #2 Injection Pump #1 |  | 0 | N/A | 0 | N/A | 1 | Injection pump Vibration Switch | 0 | N/A | 0 | N/A | [5 empty] | Murphy VS1 Vibration Switch preinstalled on inew njection pump
* | P-701 cont. | PID-1001 | Well #2 Injection Pump #1 |  | 0 | N/A | 0 | N/A | 1 | Injection pump Oillevel Switch | 0 | N/A | 0 | N/A | [5 empty] | Murphy VS1 Vibration Switch preinstalled on inew njection pump
* | P-701 cont. | PID-1001 | Well #2 Injection Pump #1 |  | 0 | N/A | 0 | N/A | 1 | Injection pump Lube Box Level Switch | 0 | N/A | 0 | N/A | [5 empty] | Murphy VS1 Vibration Switch preinstalled on inew njection pump
P-703
* | P-703 cont. | PID-1001 | Well #2 Injection Pump #2 |  | 0 | N/A | 0 | N/A | 1 | Injection pump Vibration Switch | 0 | N/A | 0 | N/A | [5 empty] | Murphy VS1 Vibration Switch preinstalled on inew njection pump
* | P-703 cont. | PID-1002 | Well #2 Injection Pump #2 |  | 0 | N/A | 0 | N/A | 1 | Injection pump Oillevel Switch | 0 | N/A | 0 | N/A | [5 empty] | Murphy VS1 Vibration Switch preinstalled on inew njection pump
* | P-703 cont. | PID-1003 | Well #2 Injection Pump #2 |  | 0 | N/A | 0 | N/A | 1 | Injection pump Lube Box Level Switch | 0 | N/A | 0 | N/A | [5 empty] | Murphy VS1 Vibration Switch preinstalled on inew njection pump
P-705
* | P-705 cont. | PID-1001 | Well #2 Injection Pump #3 |  | 0 | N/A | 0 | N/A | 1 | Injection pump Vibration Switch | 0 | N/A | 0 | N/A | [5 empty] | Murphy VS1 Vibration Switch preinstalled on inew njection pump
* | P-705 cont. | PID-1001 | Well #2 Injection Pump #3 |  | 0 | N/A | 0 | N/A | 1 | Injection pump Oillevel Switch | 0 | N/A | 0 | N/A | [5 empty] | Murphy VS1 Vibration Switch preinstalled on inew njection pump
* | P-705 cont. | PID-1001 | Well #2 Injection Pump #3 |  | 0 | N/A | 0 | N/A | 1 | Injection pump Lube Box Level Switch | 0 | N/A | 0 | N/A | [5 empty] | Murphy VS1 Vibration Switch preinstalled on inew njection pump
P-707
* | P-707 cont. | PID-1001 | Well #2 Injection Pump #4 |  | 0 | N/A | 0 | N/A | 1 | Injection pump Vibration Switch | 0 | N/A | 0 | N/A | [5 empty] | Murphy VS1 Vibration Switch preinstalled on inew njection pump
* | P-707 cont. | PID-1001 | Well #2 Injection Pump #4 |  | 0 | N/A | 0 | N/A | 1 | Injection pump Oillevel Switch | 0 | N/A | 0 | N/A | [5 empty] | Murphy VS1 Vibration Switch preinstalled on inew njection pump
* | P-707 cont. | PID-1001 | Well #2 Injection Pump #4 |  | 0 | N/A | 0 | N/A | 1 | Injection pump Lube Box Level Switch | 0 | N/A | 0 | N/A | [5 empty] | Murphy VS1 Vibration Switch preinstalled on inew njection pump
* | containment area
|  |  | inside containment water level |  | 0 | N/A |  |  | 1 | Containment area water level alarm | 0 | N/A | 0 | N/A
|  |  | pipeline valve |  | 0 | N/A |  |  | 1 | MOV Status | 0 | N/A | 0 | N/A
[5 empty] | Total-AI |  | Total-AO |  | Total-DI |  | Total-DO |  | Total-MB Drops
[5 empty] | 27 |  | 0 |  | 52 |  | 13 |  | 19
I/O not inculed in PID
Instrumentation not listed on current PID

## Not for Use (hidden)
Device Name Here
Column1 | Tag | PID | MFG | P/N | QTY | Equipment | Column4 | Column5 | Column6 | Column7 | Column8
0
|  |  |  | Total in Use | 0
Device Name Here
Column1 | Tag | PID | MFG | P/N | QTY | Equipment | Column4 | Column5 | Column6 | Column7 | Column8
0
|  |  |  | Total in Use | 0

## Signal List (hidden)
Rev | Tag | PID | Equipment | Signal Type | Analog | DI | DO | MB | Signal Use | PLC / HMI Function | Notes
| P-100 | PID-1000 | Offload Pump | DO |  |  | 1 |  | Start Command to motor starter | Auto & Manual Control | REQUIRED--aux contact/status (m.myers)
| P-100 cont. | PID-1000 | Offload Pump | DI |  | 1 |  |  | Run feedback from motor starter | Run Status, Fail to Start Alarm | REQUIRED--aux contact/status (m.myers)
| P-100 cont. | PID-1001 | Offload Pump | DI |  | 1 |  |  | Start Trans action | Start Transaction Switch | Add option on HMI
| P-100 cont. | PID-1002 | Offload Pump | DI |  | 1 |  |  | EndTrans action | End Transaction Switch | Add option on HMI
| P-101 | PID-1000 | Offload Pump | DO |  |  | 1 |  | Start Command to motor starter | Auto & Manual Control | REQUIRED--aux contact/status (m.myers)
| P-101 cont. | PID-1000 | Offload Pump | DI |  | 1 |  |  | Run feedback from motor starter | Run Status, Fail to Start Alarm | REQUIRED--aux contact/status (m.myers)
| P-101 cont. | PID-1001 | Offload Pump | DI |  | 1 |  |  | Start Trans action | Start Transaction Switch | Add option on HMI
| P-101 cont. | PID-1002 | Offload Pump | DI |  | 1 |  |  | EndTrans action | End Transaction Switch | Add option on HMI
| P-102 | PID-1000 | Offload Pump | DO |  |  | 1 |  | Start Command to motor starter | Auto & Manual Control | REQUIRED--aux contact/status (m.myers)
| P-102 cont. | PID-1000 | Offload Pump | DI |  | 1 |  |  | Run feedback from motor starter | Run Status, Fail to Start Alarm | REQUIRED--aux contact/status (m.myers)
| P-102 cont. | PID-1001 | Offload Pump | DI |  | 1 |  |  | Start Trans action | Start Transaction Switch | Add option on HMI
| P-102 cont. | PID-1002 | Offload Pump | DI |  | 1 |  |  | EndTrans action | End Transaction Switch | Add option on HMI
| P-300 | PID-1000 | Transfer Pump | DO |  |  | 1 |  | Start Command to motor starter | Auto & Manual Control | REQUIRED--aux contact/status (m.myers)
| P-300 cont. | PID-1000 | Transfer Pump | DI |  | 1 |  |  | Run feedback from motor starter | Run Status, Fail to Start Alarm | REQUIRED--aux contact/status (m.myers)
| P-300 cont. | PID-1001 | Transfer Pump | DI |  | 1 |  |  | Start Trans action | Start Transaction Switch | Add option on HMI
| P-300 cont. | PID-1002 | Transfer Pump | DI |  | 1 |  |  | EndTrans action | End Transaction Switch | Add option on HMI
| P-301 | PID-1000 | Transfer Pump | DO |  |  | 1 |  | Start Command to motor starter | Auto & Manual Control | REQUIRED--aux contact/status (m.myers)
| P-301 cont. | PID-1000 | Transfer Pump | DI |  | 1 |  |  | Run feedback from motor starter | Run Status, Fail to Start Alarm | REQUIRED--aux contact/status (m.myers)
| P-301 cont. | PID-1001 | Transfer Pump | DI |  | 1 |  |  | Start Trans action |  | Add option on HMI
| P-301 cont. | PID-1002 | Transfer Pump | DI |  | 1 |  |  | EndTrans action |  | Add option on HMI
| P-600 | PID-1001 | Well #1 Injection Charge Pump | DI |  | 1 | 1 |  | Start Command to motor starter | Auto & Manual Control | HOA installed on drive & pump Panel(RUN/STOP--status, fault, speed, amps,hz)
| P-600 cont. | PID-1001 | Well #1 Injection Charge Pump | DI |  |  |  |  | Run feedback from motor starter | Run Status, Fail to Start Alarm | RUN/STOP--status, fault, speed, amps,hz
| P-601 | PID-1001 | Well #1 Injection Pump #1 | MB |  |  |  | 1 | Start Command to Drive | Auto & Manual Control | RUN/STOP--status, fault, speed, amps,hz
| P-601 cont. | PID-1001 | Well #1 Injection Pump #1 | MB |  |  |  | 1 | Run feedback from Drive | Run Status, Fail to Start Alarm | RUN/STOP--status, fault, speed, amps,hz
| P-602 | PID-1001 | Well #1 Injection Pump #2 | MB |  |  |  | 1 | Start Command to motor starter | Auto & Manual Control | RUN/STOP--status, fault, speed, amps,hz
| P-602 cont. | PID-1001 | Well #1 Injection Pump #2 | MB |  |  |  | 1 | Run feedback from motor starter | Run Status, Fail to Start Alarm | RUN/STOP--status, fault, speed, amps,hz
| P-700 | PID-1001 | Well #2 Injection Charge Pump #1 | DI |  | 1 |  |  | Start Command to motor starter | Auto & Manual Control | RUN/STOP--status, fault, speed, amps,hz
| P-700 cont. | PID-1001 | Well #2 Injection Charge Pump #1 | DI |  | 1 |  |  | Run feedback from motor starter | Run Status, Fail to Start Alarm | RUN/STOP--status, fault, speed, amps,hz
| P-701 | PID-1001 | Well #2 Injection Pump #1 | MB |  |  |  |  | Start Command to motor starter | Auto & Manual Control | RUN/STOP--status, fault, speed, amps,hz
| P-701 cont. | PID-1001 | Well #2 Injection Pump #1 | MB |  |  |  |  | Run feedback from motor starter | Run Status, Fail to Start Alarm | RUN/STOP--status, fault, speed, amps,hz
| P-702 | PID-1001 | Well #2 Injection Charge Pump #2 | MB |  | 1 |  |  | Start Command to motor starter | Auto & Manual Control | RUN/STOP--status, fault, speed, amps,hz
| P-702 cont. | PID-1001 | Well #2 Injection Charge Pump #2 | MB |  | 1 |  |  | Run feedback from motor starter | Run Status, Fail to Start Alarm | RUN/STOP--status, fault, speed, amps,hz
| P-703 | PID-1001 | Well #2 Injection Pump #2 | MB |  |  |  |  | Start Command to motor starter | Auto & Manual Control | RUN/STOP--status, fault, speed, amps,hz
| P-703 cont. | PID-1001 | Well #2 Injection Pump #2 | MB |  |  |  |  | Run feedback from motor starter | Run Status, Fail to Start Alarm | RUN/STOP--status, fault, speed, amps,hz
| P-704 | PID-1001 | Well #2 Injection Charge Pump #3 | MB |  | 1 |  |  | Start Command to motor starter | Auto & Manual Control | RUN/STOP--status, fault, speed, amps,hz
| P-704 cont. | PID-1001 | Well #2 Injection Charge Pump #3 | MB |  | 1 |  |  | Run feedback from motor starter | Run Status, Fail to Start Alarm | RUN/STOP--status, fault, speed, amps,hz
| P-705 | PID-1001 | Well #2 Injection Pump #3 | MB |  |  |  |  | Start Command to motor starter | Auto & Manual Control | RUN/STOP--status, fault, speed, amps,hz
| P-705 cont. | PID-1001 | Well #2 Injection Pump #3 | MB |  |  |  |  | Run feedback from motor starter | Run Status, Fail to Start Alarm | RUN/STOP--status, fault, speed, amps,hz
| P-706 | PID-1001 | Well #2 Injection Charge Pump #4 | MB |  | 1 |  |  | Start Command to motor starter | Auto & Manual Control | RUN/STOP--status, fault, speed, amps,hz
| P-706 cont. | PID-1001 | Well #2 Injection Charge Pump #4 | MB |  | 1 |  |  | Run feedback from motor starter | Run Status, Fail to Start Alarm | RUN/STOP--status, fault, speed, amps,hz
| P-707 | PID-1001 | Well #2 Injection Pump #4 | MB |  |  |  |  | Start Command to motor starter | Auto & Manual Control | RUN/STOP--status, fault, speed, amps,hz
| P-707 cont. | PID-1001 | Well #2 Injection Pump #4 | MB |  |  |  |  | Run feedback from motor starter | Run Status, Fail to Start Alarm | RUN/STOP--status, fault, speed, amps,hz
| P-103 | PID-1000 | Drain Sump Pump | N/A |  |  |  |  | No control needed. | None
| P-105 | PID-1000 | Containment Sump Pump | N/A |  |  |  |  | No control needed. | None
| LSH-001 | PID-1000 | Buffer Tank TK-001 | DI |  |  |  |  | High Level | Status and High Level Alarm | Is this a float or tuning fork style that need separate 24VDC power?
| LSH-002 | PID-1000 | Buffer Tank TK-002 | DI |  |  |  |  | High Level | Status and High Level Alarm | Is this a float or tuning fork style that need separate 24VDC power?
| LSH-003 | PID-1000 | Buffer Tank TK-003 | DI |  |  |  |  | High Level | Status and High Level Alarm | Is this a float or tuning fork style that need separate 24VDC power?
| LSH-004 | PID-1000 | Buffer Tank TK-004 | DI |  |  |  |  | High Level | Status and High Level Alarm | Is this a float or tuning fork style that need separate 24VDC power?
| LSH-005 | PID-1000 | Buffer Tank TK-005 | DI |  |  |  |  | High Level | Status and High Level Alarm | Is this a float or tuning fork style that need separate 24VDC power?
| LSH-006 | PID-1000 | Buffer Tank TK-006 | DI |  |  |  |  | High Level | Status and High Level Alarm | Is this a float or tuning fork style that need separate 24VDC power?
| LSH-007 | PID-1000 | Buffer Tank TK-007 | DI |  |  |  |  | High Level | Status and High Level Alarm | Is this a float or tuning fork style that need separate 24VDC power?
| LSH-008 | PID-1000 | Buffer Tank TK-008 | DI |  |  |  |  | High Level | Status and High Level Alarm | Is this a float or tuning fork style that need separate 24VDC power?
| LSH-009 | PID-1001 | Clean Tank TK-009 | DI |  |  |  |  | High Level | Status and High Level Alarm | Is this a float or tuning fork style that need separate 24VDC power?
| LSH-010 | PID-1001 | Clean Tank TK-010 | DI |  |  |  |  | High Level | Status and High Level Alarm | Is this a float or tuning fork style that need separate 24VDC power?
| LSH-011 | PID-1001 | Clean Tank TK-011 (Existing) | DI |  |  |  |  | High Level | Status and High Level Alarm | Is this a float or tuning fork style that need separate 24VDC power?
| LSH-012 | PID-1001 | Clean Tank TK-012 (Existing) | DI |  |  |  |  | High Level | Status and High Level Alarm | Is this a float or tuning fork style that need separate 24VDC power?
| LSH-013 | PID-1001 | Clean Tank TK-013 (Existing) | DI |  |  |  |  | High Level | Status and High Level Alarm | Is this a float or tuning fork style that need separate 24VDC power?
| LSH-014 | PID-1001 | Clean Tank TK-014 (Existing) | DI |  |  |  |  | High Level | Status and High Level Alarm | Is this a float or tuning fork style that need separate 24VDC power?
| LSH-020 | PID-1000 | Oil Tank TK-020 | DI |  |  |  |  | High Level | Status and High Level Alarm | Is this a float or tuning fork style that need separate 24VDC power?
| LSH-021 | PID-1000 | Oil Tank TK-021 | DI |  |  |  |  | High Level | Status and High Level Alarm | Is this a float or tuning fork style that need separate 24VDC power?
| LSH-030 | PID-1000 | Gun Barrel TK-030 | DI |  |  |  |  | High Level | Status and High Level Alarm | Is this a float or tuning fork style that need separate 24VDC power?
| LSH-031 | PID-1000 | Gun Barrel TK-031 | DI |  |  |  |  | High Level | Status and High Level Alarm | Is this a float or tuning fork style that need separate 24VDC power?
| LIT-007 | PID-1000 | Buffer Tank TK-007 | AI |  |  |  |  | Level | Tank Level in %, High Level Alarm, Low Level Alarm, Enable for Pumps
| LIT-008 | PID-1000 | Buffer Tank TK-008 | AI |  |  |  |  | Level | Tank Level in %, High Level Alarm, Low Level Alarm, Enable for Pumps
| LIT-021 | PID-1000 | Oil Tank TK-021 | AI |  |  |  |  | Level | Tank Level in %, High Level Alarm, Low Level Alarm, Enable for Pumps
| LIT-030 | PID-1000 | Gun Barrel TK-030 | AI |  |  |  |  | Level | Tank Level in %, High Level Alarm, Low Level Alarm, Enable for Pumps
| LIT-031 | PID-1000 | Gun Barrel TK-031 | AI |  |  |  |  | Level | Tank Level in %, High Level Alarm, Low Level Alarm, Enable for Pumps
| LIT-013 | PID-1001 | Clean Tank TK-013 (Existing) | AI |  |  |  |  | Level | Tank Level in %, High Level Alarm, Low Level Alarm, Enable for Pumps
| LIT-014 | PID-1001 | Clean Tank TK-014 (Existing) | AI |  |  |  |  | Level | Tank Level in %, High Level Alarm, Low Level Alarm, Enable for Pumps
| PIT-601 | PID-1001 | Well #1 Injection Run Filter #1 | AI |  |  |  |  | Inlet Pressure | Pressure in PSIG, High Level Alarm, Low Level Alarm, | is this changing to a DPIT instead of 2 PITs
| PIT-602 | PID-1001 | Well #1 Injection Run Filter #1 | AI |  |  |  |  | Outlet Pressure | Pressure in PSIG, High Level Alarm, Low Level Alarm, | is this changing to a DPIT instead of 2 PITs
| PIT-607 | PID-1001 | Well #1 Injection Run Filter #2 | AI |  |  |  |  | Inlet Pressure | Pressure in PSIG, High Level Alarm, Low Level Alarm, | is this changing to a DPIT instead of 2 PITs
| PIT-608 | PID-1001 | Well #1 Injection Run Filter #2 | AI |  |  |  |  | Outlet Pressure | Pressure in PSIG, High Level Alarm, Low Level Alarm, | is this changing to a DPIT instead of 2 PITs
| PIT-621 | PID-1001 | Well #1 Injection Run Suction Header | AI |  |  |  |  | Pressure | Pressure in PSIG, High Level Alarm, Low Level Alarm,
| PIT-619 | PID-1001 | Well #1 Injection Run 1 | AI |  |  |  |  | Discharge Pressure | Pressure in PSIG, High Level Alarm, Low Level Alarm, | is this changing to a DPIT instead of 2 PITs
| PIT-629 | PID-1001 | Well #1 Injection Run 2 | AI |  |  |  |  | Discharge Pressure | Pressure in PSIG, High Level Alarm, Low Level Alarm, | is this changing to a DPIT instead of 2 PITs
| PIT-633 | PID-1001 | Well #1 Injection to well | AI |  |  |  |  | Pressure | Pressure in PSIG, High Level Alarm, Low Level Alarm,
| PIT-634 | PID-1001 | Well #1 Injection to well | AI |  |  |  |  | Pressure | Pressure in PSIG, High Level Alarm, Low Level Alarm,
| PIT-701 | PID-1001 | Well #2 Injection Run 1 Filter | AI |  |  |  |  | Inlet Pressure | Pressure in PSIG, High Level Alarm, Low Level Alarm, | is this changing to a DPIT instead of 2 PITs
| PIT-703 | PID-1001 | Well #2 Injection Run 1 Filter | AI |  |  |  |  | Outlet Pressure | Pressure in PSIG, High Level Alarm, Low Level Alarm, | is this changing to a DPIT instead of 2 PITs
| PIT-710 | PID-1001 | Well #2 Injection Run 1 | AI |  |  |  |  | Discharge Pressure | Pressure in PSIG, High Level Alarm, Low Level Alarm,
| PIT-713 | PID-1001 | Well #2 Injection Run 2 Filter | AI |  |  |  |  | Inlet Pressure | Pressure in PSIG, High Level Alarm, Low Level Alarm, | is this changing to a DPIT instead of 2 PITs
| PIT-715 | PID-1001 | Well #2 Injection Run 2 Filter | AI |  |  |  |  | Outlet Pressure | Pressure in PSIG, High Level Alarm, Low Level Alarm, | is this changing to a DPIT instead of 2 PITs
| PIT-722 | PID-1001 | Well #2 Injection Run 2 | AI |  |  |  |  | Discharge Pressure | Pressure in PSIG, High Level Alarm, Low Level Alarm,
| PIT-725 | PID-1001 | Well #2 Injection Run 3 Filter | AI |  |  |  |  | Inlet Pressure | Pressure in PSIG, High Level Alarm, Low Level Alarm, | is this changing to a DPIT instead of 2 PITs
| PIT-727 | PID-1001 | Well #2 Injection Run 3 Filter | AI |  |  |  |  | Outlet Pressure | Pressure in PSIG, High Level Alarm, Low Level Alarm, | is this changing to a DPIT instead of 2 PITs
| PIT-734 | PID-1001 | Well #2 Injection Run 3 | AI |  |  |  |  | Discharge Pressure | Pressure in PSIG, High Level Alarm, Low Level Alarm,
| PIT-737 | PID-1001 | Well #2 Injection Run 4 Filter | AI |  |  |  |  | Inlet Pressure | Pressure in PSIG, High Level Alarm, Low Level Alarm, | is this changing to a DPIT instead of 2 PITs
| PIT-739 | PID-1001 | Well #2 Injection Run 4 Filter | AI |  |  |  |  | Outlet Pressure | Pressure in PSIG, High Level Alarm, Low Level Alarm, | is this changing to a DPIT instead of 2 PITs
| PIT-746 | PID-1001 | Well #2 Injection Run 4 Filter | AI |  |  |  |  | Discharge Pressure | Pressure in PSIG, High Level Alarm, Low Level Alarm,
| PIT-750 | PID-1001 | Well #2 Injection to well | AI |  |  |  |  | Pressure | Pressure in PSIG, High Level Alarm, Low Level Alarm,
| PIT-751 | PID-1001 | Well #2 Injection to well | AI |  |  |  |  | Pressure | Pressure in PSIG, High Level Alarm, Low Level Alarm,
| FIT-700 | PID-1000 | Comstock Line | AI |  |  |  |  | Flow | Flow in GPM, Daily Total, Historical Totals | what type of meter this
| FIT-600 | PID-1001 | Well #1 Injection Run Suction Header | AI |  |  |  |  | Flow | Flow in GPM, Daily Total, Historical Totals | what type of meter this
| FIT-601 | PID-1001 | Well #1 Injection to well | AI |  |  |  |  | Flow | Flow in GPM, Daily Total, Historical Totals | what type of meter this
| FIT-700 | PID-1001 | Well #2 Injection to well | AI |  |  |  |  | Flow | Flow in GPM, Daily Total, Historical Totals | what type of meter this
[5 empty] | Total | Total | Total | Total
[5 empty] | 0 | 24 | 6 | 4
Additional Notes
Pump starters,drives should have HOA installed at drive, pump panel

## PIT
PIT-1 | Total DI | 13
Column1 | Tag | PID | MFG | P/N | Description | QTY | Equipment | Column4 | Column5 | AI | AI Signal Use | AO | AO Signal Use | DI | DI Signal Use | DO | DO Signal Use | MB | MB Signal Use
| PIT-739 | PID-1001 | Yokogawa | EJA530E-JBS7N-012EL/FU1/D1 | Yokogawa DPharp Digital Direct Mount Gauge Pressure Transmitter 0-290 PSI Min | 1 | Well #2 Injection Run 4 Filter (F-706 postfilter) In uses as DP | 0-290 PSI Min |  | 1 | Well #2 Injection Run 4 Filter (F-706 postfilter) In uses as DP | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
| PIT-737 | PID-1001 | Yokogawa | EJA530E-JBS7N-012EL/FU1/D1 | Yokogawa DPharp Digital Direct Mount Gauge Pressure Transmitter 0-290 PSI Min | 1 | Well #2 Injection Run 4 Filter (F-706 prefilter) In uses as DP | 0-290 PSI Min |  | 1 | Well #2 Injection Run 4 Filter (F-706 prefilter) In uses as DP | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
| PIT-725 | PID-1001 | Yokogawa | EJA530E-JBS7N-012EL/FU1/D1 | Yokogawa DPharp Digital Direct Mount Gauge Pressure Transmitter 0-290 PSI Min | 1 | Well #2 Injection Run 3 Filter (F-704 prefilter) In uses as DP | 0-290 PSI Min |  | 1 | Well #2 Injection Run 3 Filter (F-704 prefilter) In uses as DP | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
| PIT-727 | PID-1001 | Yokogawa | EJA530E-JBS7N-012EL/FU1/D1 | Yokogawa DPharp Digital Direct Mount Gauge Pressure Transmitter 0-290 PSI Min | 1 | Well #2 Injection Run 3 Filter (F-704 postfilter) In uses as DP | 0-290 PSI Min |  | 1 | Well #2 Injection Run 3 Filter (F-704 postfilter) In uses as DP | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
| PIT-713 | PID-1001 | Yokogawa | EJA530E-JBS7N-012EL/FU1/D1 | Yokogawa DPharp Digital Direct Mount Gauge Pressure Transmitter 0-290 PSI Min | 1 | Well #2 Injection Run 2 Filter (F-702 prefilter) In uses as DP | 0-290 PSI Min |  | 1 | Well #2 Injection Run 2 Filter (F-702 prefilter) In uses as DP | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
| PIT-715 | PID-1001 | Yokogawa | EJA530E-JBS7N-012EL/FU1/D1 | Yokogawa DPharp Digital Direct Mount Gauge Pressure Transmitter 0-290 PSI Min | 1 | Well #2 Injection Run 2 Filter (F-702 postfilter) In uses as DP | 0-290 PSI Min |  | 1 | Well #2 Injection Run 2 Filter (F-702 postfilter) In uses as DP | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
| PIT-701 | PID-1001 | Yokogawa | EJA530E-JBS7N-012EL/FU1/D1 | Yokogawa DPharp Digital Direct Mount Gauge Pressure Transmitter 0-290 PSI Min | 1 | Well #2 Injection Run 1 Filter (F-701 prefilter) In uses as DP | 0-290 PSI Min |  | 1 | Well #2 Injection Run 1 Filter (F-701 prefilter) In uses as DP | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
| PIT-703 | PID-1001 | Yokogawa | EJA530E-JBS7N-012EL/FU1/D1 | Yokogawa DPharp Digital Direct Mount Gauge Pressure Transmitter 0-290 PSI Min | 1 | Well #2 Injection Run 1 Filter (F-701 postfilter) In uses as DP | 0-290 PSI Min |  | 1 | Well #2 Injection Run 1 Filter (F-701 postfilter) In uses as DP | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
| PIT-621 | PID-1001 | Yokogawa | EJA530E-JBS7N-012EL/FU1/D1 | Yokogawa DPharp Digital Direct Mount Gauge Pressure Transmitter 0-290 PSI Min | 1 | Well #1 Injection Run Suction Header (Wellhead #1 Injection pump header) | 0-290 PSI Min |  | 1 | Well #1 Injection Run Suction Header (Wellhead #1 Injection pump header) | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
| PIT-607 | PID-1001 | Yokogawa | EJA530E-JBS7N-012EL/FU1/D1 | Yokogawa DPharp Digital Direct Mount Gauge Pressure Transmitter 0-290 PSI Min | 1 | Well #1 Injection Run Filter #2 (F-601 prefilter) In uses as DP | 0-290 PSI Min |  | 1 | Well #1 Injection Run Filter #2 (F-601 prefilter) In uses as DP | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
| PIT-608 | PID-1001 | Yokogawa | EJA530E-JBS7N-012EL/FU1/D1 | Yokogawa DPharp Digital Direct Mount Gauge Pressure Transmitter 0-290 PSI Min | 1 | Well #1 Injection Run Filter #2 (F-601 postfilter) In uses as DP | 0-290 PSI Min |  | 1 | Well #1 Injection Run Filter #2 (F-601 postfilter) In uses as DP | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
| PIT-601 | PID-1001 | Yokogawa | EJA530E-JBS7N-012EL/FU1/D1 | Yokogawa DPharp Digital Direct Mount Gauge Pressure Transmitter 0-290 PSI Min | 1 | Well #1 Injection Run Filter #1 (F-600 prefilter) In uses as DP | 0-290 PSI Min |  | 1 | Well #1 Injection Run Filter #1 (F-600 prefilter) In uses as DP | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
| PIT-602 | PID-1001 | Yokogawa | EJA530E-JBS7N-012EL/FU1/D1 | Yokogawa DPharp Digital Direct Mount Gauge Pressure Transmitter 0-290 PSI Min | 1 | Well #1 Injection Run Filter #1 (F-600 Post Filter) In uses as DP | 0-290 PSI Min |  | 1 | Well #1 Injection Run Filter #1 (F-600 Post Filter) In uses as DP | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
[12 empty] | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
[12 empty] | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
[12 empty] | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
[12 empty] | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Qty Required | 13
Total AI | 13
Total AO
Total DI
Total Do
[17 empty] | Total AI | 13
PIT-2 | Total DI | 10
Column1 | Tag | PID | MFG | P/N | Description | QTY | Equipment | Column4 | Column5 | AI | AI Signal Use | AO | AO Signal Use | DI | DI Signal Use | DO | DO Signal Use | MB | MB Signal Use
| PIT-619 | PID-1001 | Yokogawa | EJA530E-JDS7N-012EL/FU1/D1 | Yokogawa DPharp Digital Direct Mount Gauge Pressure Transmitter 0-7200 PSI Min | 1 | Well #1 Injection Run 1 (P-601 Discharge PSI) | 0-7200 PSI Min |  | 1 | Well #1 Injection Run 1 (P-601 Discharge PSI) | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
| PIT-629 | PID-1001 | Yokogawa | EJA530E-JDS7N-012EL/FU1/D1 | Yokogawa DPharp Digital Direct Mount Gauge Pressure Transmitter 0-7200 PSI Min | 1 | Well #1 Injection Run 2 (P-602 Discharge PSI) | 0-7200 PSI Min |  | 1 | Well #1 Injection Run 2 (P-602 Discharge PSI) | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
| PIT-633 | PID-1001 | Yokogawa | EJA530E-JDS7N-012EL/FU1/D1 | Yokogawa DPharp Digital Direct Mount Gauge Pressure Transmitter 0-7200 PSI Min | 1 | Well #1 Injection to well (Injection PSI) | 0-7200 PSI Min |  | 1 | Well #1 Injection to well (Injection PSI) | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
| PIT-634 | PID-1001 | Yokogawa | EJA530E-JDS7N-012EL/FU1/D1 | Yokogawa DPharp Digital Direct Mount Gauge Pressure Transmitter 0-7200 PSI Min | 1 | Well #1 Injection to well ( Anulus) | 0-7200 PSI Min |  | 1 | Well #1 Injection to well ( Anulus) | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
| PIT-710 | PID-1001 | Yokogawa | EJA530E-JDS7N-012EL/FU1/D1 | Yokogawa DPharp Digital Direct Mount Gauge Pressure Transmitter 0-7200 PSI Min | 1 | Well #2 Injection Run 1 (P-701 Discharge PSI) | 0-7200 PSI Min |  | 1 | Well #2 Injection Run 1 (P-701 Discharge PSI) | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
| PIT-722 | PID-1001 | Yokogawa | EJA530E-JDS7N-012EL/FU1/D1 | Yokogawa DPharp Digital Direct Mount Gauge Pressure Transmitter 0-7200 PSI Min | 1 | Well #2 Injection Run 2 (P-703 Discharge PSI) | 0-7200 PSI Min |  | 1 | Well #2 Injection Run 2 (P-703 Discharge PSI) | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
| PIT-734 | PID-1001 | Yokogawa | EJA530E-JDS7N-012EL/FU1/D1 | Yokogawa DPharp Digital Direct Mount Gauge Pressure Transmitter 0-7200 PSI Min | 1 | Well #2 Injection Run 3 (P-705 Discharge PSI) | 0-7200 PSI Min |  | 1 | Well #2 Injection Run 3 (P-705 Discharge PSI) | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
| PIT-746 | PID-1001 | Yokogawa | EJA530E-JDS7N-012EL/FU1/D1 | Yokogawa DPharp Digital Direct Mount Gauge Pressure Transmitter 0-7200 PSI Min | 1 | Well #2 Injection Run 4 Filter (P-706 Discharge PSI) | 0-7200 PSI Min |  | 1 | Well #2 Injection Run 4 Filter (P-706 Discharge PSI) | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
| PIT-750 | PID-1001 | Yokogawa | EJA530E-JDS7N-012EL/FU1/D1 | Yokogawa DPharp Digital Direct Mount Gauge Pressure Transmitter 0-7200 PSI Min | 1 | Well #2 Injection to well (Injection PSI) | 0-7200 PSI Min |  | 1 | Well #2 Injection to well (Injection PSI) | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
| PIT-751 | PID-1001 | Yokogawa | EJA530E-JDS7N-012EL/FU1/D1 | Yokogawa DPharp Digital Direct Mount Gauge Pressure Transmitter 0-7200 PSI Min | 1 | Well #2 Injection to well (Anulus PS) | 0-7200 PSI Min |  | 1 | Well #2 Injection to well (Anulus PS) | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
[12 empty] | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
[12 empty] | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
[17 empty] | Total AI | 10
| Sheet Total | 23

## LSH
LSH | LSH | Total DI | 18
Column1 | Tag | PID | MFG | P/N | Description | QTY | Equipment | MFG2 | Column5 | AI | AI Signal Use | AO | AO Signal Use | DI | DI Signal Use | DO | DO Signal Use | MB | MB Signal Use
| LSH-001 | PID-1000 | Magnetrol | 961-2DA1-030 w/ 9A1-A21A-012 | Echotel Model 961 Ultrasonic Level Switch | 1 | Buffer Tank TK-001 | Echotel Model 961 Ultrasonic Level Switch | [5 empty] | 1 | Status and High Level Alarm
| LSH-002 | PID-1000 | Magnetrol | 961-2DA1-030 w/ 9A1-A21A-012 | Echotel Model 961 Ultrasonic Level Switch | 1 | Buffer Tank TK-002 | Echotel Model 961 Ultrasonic Level Switch | [5 empty] | 1 | Status and High Level Alarm
| LSH-003 | PID-1000 | Magnetrol | 961-2DA1-030 w/ 9A1-A21A-012 | Echotel Model 961 Ultrasonic Level Switch | 1 | Buffer Tank TK-003 | Echotel Model 961 Ultrasonic Level Switch | [5 empty] | 1 | Status and High Level Alarm
| LSH-004 | PID-1000 | Magnetrol | 961-2DA1-030 w/ 9A1-A21A-012 | Echotel Model 961 Ultrasonic Level Switch | 1 | Buffer Tank TK-004 | Echotel Model 961 Ultrasonic Level Switch | [5 empty] | 1 | Status and High Level Alarm
| LSH-005 | PID-1000 | Magnetrol | 961-2DA1-030 w/ 9A1-A21A-012 | Echotel Model 961 Ultrasonic Level Switch | 1 | Buffer Tank TK-005 | Echotel Model 961 Ultrasonic Level Switch | [5 empty] | 1 | Status and High Level Alarm
| LSH-006 | PID-1000 | Magnetrol | 961-2DA1-030 w/ 9A1-A21A-012 | Echotel Model 961 Ultrasonic Level Switch | 1 | Buffer Tank TK-006 | Echotel Model 961 Ultrasonic Level Switch | [5 empty] | 1 | Status and High Level Alarm
| LSH-007 | PID-1000 | Magnetrol | 961-2DA1-030 w/ 9A1-A21A-012 | Echotel Model 961 Ultrasonic Level Switch | 1 | Buffer Tank TK-007 | Echotel Model 961 Ultrasonic Level Switch | [5 empty] | 1 | Status and High Level Alarm
| LSH-008 | PID-1000 | Magnetrol | 961-2DA1-030 w/ 9A1-A21A-012 | Echotel Model 961 Ultrasonic Level Switch | 1 | Buffer Tank TK-008 | Echotel Model 961 Ultrasonic Level Switch | [5 empty] | 1 | Status and High Level Alarm
| LSH-009 | PID-1001 | Magnetrol | 961-2DA1-030 w/ 9A1-A21A-012 | Echotel Model 961 Ultrasonic Level Switch | 1 | Clean Tank TK-009 | Echotel Model 961 Ultrasonic Level Switch | [5 empty] | 1 | Status and High Level Alarm
| LSH-010 | PID-1001 | Magnetrol | 961-2DA1-030 w/ 9A1-A21A-012 | Echotel Model 961 Ultrasonic Level Switch | 1 | Clean Tank TK-010 | Echotel Model 961 Ultrasonic Level Switch | [5 empty] | 1 | Status and High Level Alarm
| LSH-011 | PID-1001 | Magnetrol | 961-2DA1-030 w/ 9A1-A21A-012 | Echotel Model 961 Ultrasonic Level Switch | 1 | Clean Tank TK-011 (Existing) | Echotel Model 961 Ultrasonic Level Switch | [5 empty] | 1 | Status and High Level Alarm
| LSH-012 | PID-1001 | Magnetrol | 961-2DA1-030 w/ 9A1-A21A-012 | Echotel Model 961 Ultrasonic Level Switch | 1 | Clean Tank TK-012 (Existing) | Echotel Model 961 Ultrasonic Level Switch | [5 empty] | 1 | Status and High Level Alarm
| LSH-013 | PID-1001 | Magnetrol | 961-2DA1-030 w/ 9A1-A21A-012 | Echotel Model 961 Ultrasonic Level Switch | 1 | Clean Tank TK-013 (Existing) | Echotel Model 961 Ultrasonic Level Switch | [5 empty] | 1 | Status and High Level Alarm
| LSH-014 | PID-1001 | Magnetrol | 961-2DA1-030 w/ 9A1-A21A-012 | Echotel Model 961 Ultrasonic Level Switch | 1 | Clean Tank TK-014 (Existing) | Echotel Model 961 Ultrasonic Level Switch | [5 empty] | 1 | Status and High Level Alarm
| LSH-020 | PID-1000 | Magnetrol | 961-2DA1-030 w/ 9A1-A21A-012 | Echotel Model 961 Ultrasonic Level Switch | 1 | Oil Tank TK-020 | Echotel Model 961 Ultrasonic Level Switch | [5 empty] | 1 | Status and High Level Alarm
| LSH-021 | PID-1000 | Magnetrol | 961-2DA1-030 w/ 9A1-A21A-012 | Echotel Model 961 Ultrasonic Level Switch | 1 | Oil Tank TK-021 | Echotel Model 961 Ultrasonic Level Switch | [5 empty] | 1 | Status and High Level Alarm
| LSH-030 | PID-1000 | Magnetrol | 961-2DA1-030 w/ 9A1-A21A-012 | Echotel Model 961 Ultrasonic Level Switch | 1 | Gun Barrel TK-030 | Echotel Model 961 Ultrasonic Level Switch | [5 empty] | 1 | Status and High Level Alarm
| LSH-031 | PID-1000 | Magnetrol | 961-2DA1-030 w/ 9A1-A21A-012 | Echotel Model 961 Ultrasonic Level Switch | 1 | Gun Barrel TK-031 | Echotel Model 961 Ultrasonic Level Switch | [5 empty] | 1 | Status and High Level Alarm
[18 empty] | Total DI | 18
|  | Sheet Total | 18

## LIT
| LIT | Total MB | 7
Column1 | Tag | PID | MFG | P/N | QTY | Equipment | Description | Column5 | AI | AI Signal Use | AO | AO Signal Use | DI | DI Signal Use | DO | DO Signal Use | MB | MB Signal Use
| LIT-007 | PID-1000 | Magnetrol | 706-540A-310 | 1 | Buffer Tank TK-007 | ECLIPSE 4th Generation Guided Wave Radar Modbus |  | 1 | Tank Level/Interface | [6 empty] | 1 | Level and Interface
| LIT-008 | PID-1000 | Magnetrol | 706-540A-310 | 1 | Buffer Tank TK-008 | ECLIPSE 4th Generation Guided Wave Radar Modbus |  | 1 | Tank Level/Interface | [6 empty] | 1 | Level and Interface
| LIT-021 | PID-1000 | Magnetrol | 706-540A-310 | 1 | Oil Tank TK-021 | ECLIPSE 4th Generation Guided Wave Radar Modbus |  | 1 | Tank Level/Interface | [6 empty] | 1 | Level and Interface
| LIT-030 | PID-1000 | Magnetrol | 706-540A-310 | 1 | Gun Barrel TK-030 | ECLIPSE 4th Generation Guided Wave Radar Modbus |  | 1 | Tank Level/Interface | [6 empty] | 1 | Level and Interface
| LIT-031 | PID-1000 | Magnetrol | 706-540A-310 | 1 | Gun Barrel TK-031 | ECLIPSE 4th Generation Guided Wave Radar Modbus |  | 1 | Tank Level/Interface | [6 empty] | 1 | Level and Interface
| LIT-013 | PID-1001 | Magnetrol | 706-540A-310 | 1 | Clean Tank TK-013 (Existing) | ECLIPSE 4th Generation Guided Wave Radar Modbus |  | 1 | Tank Level/Interface | [6 empty] | 1 | Level and Interface
| LIT-014 | PID-1000 | Magnetrol | 706-540A-309 | 1 | Clean Tank TK-014 (Existing) | ECLIPSE 4th Generation Guided Wave Radar Modbus |  | 1 | Tank Level/Interface | [6 empty] | 1 | Level and Interface
[16 empty] | Total | 7

## FIT
FIT | Total MB | 4
Column1 | Tag | PID | MFG | P/N | Description | QTY | Equipment | Column4 | Column5 | AI | AI Signal Use | AO | AO Signal Use | DI | DI Signal Use | DO | DO Signal Use | MB | MB Signal Use
| FIT-100 | PID-1000 | Yokogawa | AXG150-CASF2BA1AL212B-2M011/GRL/MC | ADMAG TI Series Magnetic Flowmeter 150mm (6 in.) | 1 | Comstock Line | [10 empty] | 1 | Comstock PipeLine Flow Meter
| FIT-600 | PID-1001 | Yokogawa | AXG150-CASF2BA1AL212B-2M011/GRL/MC | ADMAG TI Series Magnetic Flowmeter 150mm (6 in.) | 1 | Well #1 Injection Run Suction Header | [10 empty] | 1 | P-601/602 Suction Header
| FIT-601 | PID-1001 | Yokogawa | AXG150-CASF2BA1AL212B-2M011/GRL/MC | ADMAG TI Series Magnetic Flowmeter 150mm (6 in.) | 1 | Well #1 Injection to well | [10 empty] | 1 | P-601/602 Discharge Header
| FIT-700 | PID-1001 | Yokogawa | AXG150-CASF2BA1AL212B-2M011/GRL/MC | ADMAG TI Series Magnetic Flowmeter 150mm (6 in.) | 1 | Well #2 Injection to well | [10 empty] | 1 | Injection Well #2 Flowmeter
[18 empty] | Total | 4
| Sheet Total | 4

## MOV
MOV | Total DI | 13
Not Listed P*ID | Tag | PID | MFG | P/N | Description | QTY | Equipment | Column4 | Column5 | AI | AI Signal Use | AO | AO Signal Use | DI | DI Signal Use | DO | DO Signal Use | MB | MB Signal Use
* | CV-xxx | PID-1000 | J-Flow Controls | C-2F33FTTTF1LD | 6", Ball Valve, ANSI 150, TRIAC ACTUATOR 7000 MOV | 1 | ComStock Pipe line | [6 empty] | 1 | Valve Status | 1 | Valve Operation
| CV-700 | PID-1000 | J-Flow Controls | C-2F33FTTTF1LD | 6", Ball Valve, ANSI 150, TRIAC ACTUATOR 7000 MOV | 1 | P-700 Charge Pump | [6 empty] | 1 | Valve Status | 1 | Valve Operation
| CV-708 | PID-1000 | J-Flow Controls | C-2F33FTTTF1LD | 6", Ball Valve, ANSI 150, TRIAC ACTUATOR 7000 MOV | 1 | P-701 Inj Pump | [6 empty] | 1 | Valve Status | 1 | Valve Operation
| CV-712 | PID-1000 | J-Flow Controls | C-2F33FTTTF1LD | 6", Ball Valve, ANSI 150, TRIAC ACTUATOR 7000 MOV | 1 | P-702 Charge Pump | [6 empty] | 1 | Valve Status | 1 | Valve Operation
| CV-720 | PID-1000 | J-Flow Controls | C-2F33FTTTF1LD | 6", Ball Valve, ANSI 150, TRIAC ACTUATOR 7000 MOV | 1 | P-703 Inj Pump | [6 empty] | 1 | Valve Status | 1 | Valve Operation
| CV-724 | PID-1000 | J-Flow Controls | C-2F33FTTTF1LD | 6", Ball Valve, ANSI 150, TRIAC ACTUATOR 7000 MOV | 1 | P-704 Charge Pump | [6 empty] | 1 | Valve Status | 1 | Valve Operation
| CV-732 | PID-1000 | J-Flow Controls | C-2F33FTTTF1LD | 6", Ball Valve, ANSI 150, TRIAC ACTUATOR 7000 MOV | 1 | P-705 Inj Pump | [6 empty] | 1 | Valve Status | 1 | Valve Operation
| CV-736 | PID-1000 | J-Flow Controls | C-2F33FTTTF1LD | 6", Ball Valve, ANSI 150, TRIAC ACTUATOR 7000 MOV | 1 | P-706 Charge Pump | [6 empty] | 1 | Valve Status | 1 | Valve Operation
| CV-744 | PID-1000 | J-Flow Controls | C-2F33FTTTF1LD | 6", Ball Valve, ANSI 150, TRIAC ACTUATOR 7000 MOV | 1 | P-707 Inj Pump | [6 empty] | 1 | Valve Status | 1 | Valve Operation
| CV-600 | PID-1000 | J-Flow Controls | C-2F33FTTTF1LD | 6", Ball Valve, ANSI 150, TRIAC ACTUATOR 7000 MOV | 1 | F-600 Injection Filter | [6 empty] | 1 | Valve Status | 1 | Valve Operation
| CV-606 | PID-1000 | J-Flow Controls | C-2F33FTTTF1LD | 6", Ball Valve, ANSI 150, TRIAC ACTUATOR 7000 MOV | 1 | F-601 Injection Filter | [6 empty] | 1 | Valve Status | 1 | Valve Operation
| CV-618 | PID-1000 | J-Flow Controls | C-2F33FTTTF1LD | 6", Ball Valve, ANSI 150, TRIAC ACTUATOR 7000 MOV | 1 | P-601 Injection pump header | [6 empty] | 1 | Valve Status | 1 | Valve Operation
| CV-627 | PID-999 | J-Flow Controls | C-2F33FTTTF1LD | 6", Ball Valve, ANSI 150, TRIAC ACTUATOR 7000 MOV | 1 | P-602 Injection pump header | [6 empty] | 1 | Valve Status | 1 | Valve Operation
1
[13 empty] | Total | 13 | Total | 14

## OLS
OLS | Total DI | 6 |  |  | Pump Oil Level
Not Listed P*ID | Tag | PID | MFG | P/N | Description | QTY | Equipment | Column4 | Column5 | AI | AI Signal Use | AO | AO Signal Use | DI | DI Signal Use | DO | DO Signal Use | MB | MB Signal Use
| OLS-601 | PID-1001 | Murphy | L-129 | Pump Oil Level Switch | 1 | P-601 Oil Level Switch | [6 empty] | 1 | Injection pump low power end oil level
| OLS-602 | PID-1001 | Murphy | L-129 | Pump Oil Level Switch | 1 | P-602 Oil Level Switch | [6 empty] | 1 | Injection pump low power end oil level
| OLS-701 | PID-1001 | Murphy | L-129 | Pump Oil Level Switch | 1 | P-701 Oil Level Switch | [6 empty] | 1 | Injection pump low power end oil level
| OLS-703 | PID-1001 | Murphy | L-129 | Pump Oil Level Switch | 1 | P-703 Oil Level Switch | [6 empty] | 1 | Injection pump low power end oil level
| OLS-705 | PID-1001 | Murphy | L-129 | Pump Oil Level Switch | 1 | P-705 Oil Level Switch | [6 empty] | 1 | Injection pump low power end oil level
| OLS-707 | PID-1001 | Murphy | L-129 | Pump Oil Level Switch | 1 | P-707 Oil Level Switch | [6 empty] | 1 | Injection pump low power end oil level
6
| Sheet Total | 6

## VS
VS | Total DI | 6 |  |  | Vibration Switch
Not Listed P*ID | Tag | PID | MFG | P/N | Description | QTY | Equipment | Column4 | Column5 | AI | AI Signal Use | AO | AO Signal Use | DI | DI in use as
| OLS-601 |  | Murphy | VS-1 | Injection Pump Vibration Switch | 1 | P-601 Vibration Switch | [6 empty] | 1 | injection pump high vibration switch
| OLS-602 |  | Murphy | VS-1 | Injection Pump Vibration Switch | 1 | P-601 Vibration Switch | [6 empty] | 1 | injection pump high vibration switch
| OLS-701 |  | Murphy | VS-1 | Injection Pump Vibration Switch | 1 | P-601 Vibration Switch | [6 empty] | 1 | injection pump high vibration switch
| OLS-702 |  | Murphy | VS-1 | Injection Pump Vibration Switch | 1 | P-601 Vibration Switch | [6 empty] | 1 | injection pump high vibration switch
| OLS-703 |  | Murphy | VS-1 | Injection Pump Vibration Switch | 1 | P-601 Vibration Switch | [6 empty] | 1 | injection pump high vibration switch
| OLS-705 |  | Murphy | VS-1 | Injection Pump Vibration Switch | 1 | P-601 Vibration Switch | [6 empty] | 1 | injection pump high vibration switch
| Sheet Total | 6

## LLS
LLS | Total DI | 6 |  |  | Pump Lube Level
Not Listed P*ID | Tag | PID | MFG | P/N | Description | QTY | Equipment | Column4 | Column5 | AI | AI Signal Use | AO | AO Signal Use | DI
| OLS-601 |  | Murphy | VS-1 | Injection Pump Lube Level Switch | 1 | P-601 Lube Level Switch | [6 empty] | 1
| OLS-602 |  | Murphy | VS-1 | Injection Pump Lube Level Switch | 1 | P-601 Lube Level Switch | [6 empty] | 1
| OLS-701 |  | Murphy | VS-1 | Injection Pump Lube Level Switch | 1 | P-601 Lube Level Switch | [6 empty] | 1
| OLS-703 |  | Murphy | VS-1 | Injection Pump Lube Level Switch | 1 | P-601 Lube Level Switch | [6 empty] | 1
| OLS-705 |  | Murphy | VS-1 | Injection Pump Lube Level Switch | 1 | P-601 Lube Level Switch | [6 empty] | 1
| OLS-707 |  | Murphy | VS-1 | Injection Pump Lube Level Switch | 1 | P-601 Lube Level Switch | [6 empty] | 1
| Sheet Total | 6

## PMPP
PMPP | Total MB | 0 |  |  | Pump Panel
Column1 | Tag | PID | MFG | P/N | Description | QTY | Equipment | Column4 | Column5 | AI | AI Signal Use | AO | AO Signal Use | DI | DI Signal Use | DO | DO Signal Use | MB | MB Signal Use
| PMPP-100 |  |  |  | P-100 Offload Pump Panel |  | P-100 Offload Pump Panel | [6 empty] | 1 | Pump Status
| PMPP-101 |  |  |  | P-101 Offload Pump Panel |  | P-101 Offload Pump Panel | [6 empty] | 1 | Pump Status
| PMPP-102 |  |  |  | P-102 Offload Pump Panel |  | P-102 Offload Pump Panel | [6 empty] | 1 | Pump Status
| PMPP -300 |  |  |  | P-300 Transfer Pump Panel |  | P-300 Transfer Pump Panel | [6 empty] | 1 | Pump Status | 1 | PLC/HMI Remote Operation
| PMPP -301 |  |  |  | P-301 Transfer Pump Panel |  | P-301 Transfer Pump Panel | [6 empty] | 1 | Pump Status | 1 | PLC/HMI Remote Operation
| PMPP-600 |  |  |  | P-600 Injection Charge Pump |  | P-600 Injection Charge Pump Panel | [7 empty] | Pump Status | 1 | PLC/HMI Remote Operation
| PMPP-700 |  |  |  | P-700 Injection Charge Pump |  | P-700 Injection Charge Pump Panel | [7 empty] | Pump Status | 1 | PLC/HMI Remote Operation
| PMPP-702 |  |  |  | P-702 Injection Charge Pump |  | P-702 Injection Charge Pump Panel | [7 empty] | Pump Status | 1 | PLC/HMI Remote Operation
| PMPP-704 |  |  |  | P-704 Injection Charge Pump |  | P-704 Injection Charge Pump Panel | [7 empty] | Pump Status | 1 | PLC/HMI Remote Operation
| PMPP-705 |  |  |  | P-705 Injection Charge Pump |  | P-705 Injection Charge PumpPanel | [7 empty] | Pump Status | 1 | PLC/HMI Remote Operation
[7 empty] | Total | [6 empty] | 5 | Total | 7 |  | Total | 0
| Sheet Total | 0
0

## Drive-VFD
DRV |  |  |  |  | VFD- Drives
Column1 | Tag | PID | MFG | P/N | Description | QTY | Equipment | Column4 | Column5 | AI | AI Signal Use | AO | AO Signal Use | DI | DI Signal Use | DO | DO Signal Use | MB | MB Signal Use
| DRV-601 | PID-1001 | Unknown | N/a |  |  | P-601 Inj Pump | [10 empty] | 1
| DRV-602 | PID-1001 | Unknown | N/a |  |  | P-602 Inj Pump | [10 empty] | 1
| DRV-701 | PID-1001 | Unknown | N/a |  |  | P-701 Inj Pump | [10 empty] | 1
| DRV-703 | PID-1001 | Unknown | N/a |  |  | P-703 Inj Pump | [10 empty] | 1
| DRV-705 | PID-1001 | Unknown | N/a |  |  | P-705 Inj Pump | [10 empty] | 1
| DRV-707 | PID-1001 | Unknown | N/a |  |  | P-707 Inj Pump | [10 empty] | 1
6

## Main Panel
Quote Title: (Use Customer Meaningful Title)
Company:
Requested by:
Contact Info: |  |  | AI Module | 3 | DI Module | 5
Date: |  |  | AO Module | 0 | DO Module | 2
Created by: |  |  | AI = | 40 | DI= | 80 |  |  |  |  | Buy/Resell
Peer Review by: |  |  | AO = | 0 | DO= | 32 |  |  |  |  | Commission
Peer Review by: | [10 empty] | Direct
|  | Is this for Buy/Resell, Rep Commission or Direct? | Direct |  | Starting Margin = | 25% |  | S
Parts List Descriptions (for Formal Quote) | Vendor Name (or Stock)- (internal use) | Part Numbers (Internal Use) | Cost/ea. | Qty | Total Cost | TAS Margin (%) | Total Sell Price |  |  | Quote Description
Concept Single-Door Enclosure, 60.00x36.00x12.00, Gray, Steel | Reynolds | CSD603612 | 584.81 | 1 | 584.81 | 25% | 779.7467 |  | FALSE | Material: (Use Salesy terms and simplify by grouping like items (i.e., 20 Meter Cable Sets, not all the pieces))
Concept Panel, fits 60.00x36.00, White, Steel | Reynolds | CP6036 | 167.63 | 1 | 167.63 | 25% | 223.5067 |  | FALSE | -
Fused LED 2 layer Phoenix Contact Terminal Block | Graybar | 3214366 | 9.15 | 112 | 1024.8 | 25% | 1366.4 |  | FALSE | -
Fused LED 3 layer Phoenix Contact Terminal Block | Graybar | 3214321 | 11.07 | 40 | 442.8 | 25% | 590.4 |  | FALSE | -
Fused LED 2 layer Phoenix Contact Terminal Block (DC Distribution) | Graybar | 3214366 | 9.15 | 20 | 183 | 25% | 244 |  | FALSE | -
Fused LED 2 layer Phoenix Contact Terminal Block (Modbus Power) | Graybar | 3214366 | 9.15 | 32 | 292.8 | 25% | 390.4 |  | FALSE | -
2 Layer Feed Through Terminal Block | Graybar | 3214360 | 8.88 | 32 | 284.16 | 25% | 378.88 |  | FALSE | -
PLC Relays | Graybar | 2966171 | 10.51 | 32 | 336.32 | 25% | 448.4267
20A Circuit Breaker | Reynolds | 1489-M1C200 | 18.39 | 1 | 18.39 | 25% | 24.52 |  | FALSE | Scope: (Record everything you told the customer it would do AND what you plan for it to do)
CompactLogix 5380 Controller, 2MB, 16 I/Os, 40 nodes, Standard | Reynolds | 5069-L320ER | 3436.46 | 1 | 3436.46 | 25% | 4581.9467
Power terminal RTB kit for CompactLogix 5380 Controllers and 5069-AEN2TR. Contains both 4 and 6 pin Screw type RTB | Reynolds | 5069-RTB64-SCREW | 33.36 | 1 | 33.36 | 25% | 44.48
5069 Compact I/O 16 Channel 24VDC Sink Input Module, 100µs response, up to 500hz simple counter | Reynolds | 5069-IB16 | 259.57 | 5 | 1297.85 | 25% | 1730.4667
5069 Compact I/O 18 pins Screw type terminal block kit | Reynolds | 5069-RTB18-SCREW | 60.99 | 11 | 670.89 | 25% | 894.52
5069 Compact I/O 16 Channel 24VDC Source Output Module, 100µs response, 2 tier fault mode, hold last state | Reynolds | 5069-OB16 | 335.58 | 2 | 671.16 | 25% | 894.88
5069 Compact I/O 8 Channel Voltage/Current Analog Input Module, 16 bit resolution, 1ms channel update rate, analog scaling | Reynolds | 5069-IF8 | 855.71 | 4 | 3422.84 | 25% | 4563.7867
15" HMI with 4 Serial, 2 Ethernet, 2 USB Host, USB Device, Web Server Data Logging | Red Lion | CR30001500000420 | 2640.95 | 1 | 2640.95 | 25% | 3521.2667
PULS 24VDC, 20A Power Supply | PULS | CP20.241 | 276.45 | 1 | 276.45 | 25% | 368.6 |  | FALSE
16 port unmanaged Ethernet Switch | Red Lion | 116TX | 369.25 | 1 | 369.25 | 25% | 492.3333 |  | FALSE
Enclosure Light | Banner | WLB32C285PB | 53.9 | 2 | 107.8 | 25% | 143.7333
Enclosure Light Magnet | Banner | LMBWLB32MAG | 12.6 | 2 | 25.2 | 25% | 33.6
Door Intrusion Switch | SCE | SCE-LSA | 26.65 | 2 | 53.3 | 25% | 71.0667
Panduit/Din Rail/Wire |  |  | 500 | 1 | 500 | 25% | 666.6667
Engraved Placards |  |  | 50 | 1 | 50 | 25% | 66.6667 |  | FALSE
ESTOP BUTTON - EATON | Allied/Summit | 10250T5B63-1X | 63.98 | 1 | 63.98 | 25% | 85.3067 |  | FALSE
ESTOP SHROUD - YELLOW LARGE - EATON | Allied/Summit | 10250ED1241 | 63.3 | 1 | 63.3 | 25% | 84.4 |  | FALSE
[5 empty] | 0 | 25% | 0 |  | FALSE
Misc. |  |  | 500 | 1 | 500 | 25% | 666.6667 |  | FALSE
[5 empty] | 0 | 25% | 0 |  | FALSE
|  | Material Total |  |  | 17517.5 | 25% | 23356.6667 |  | 0
|  | Shop Labor Cost | 52.5 | 50 | 2625 | 25% | 3500
|  | Engineering and Programming Labor Cost | 70 | 0 | 0 | 25% | 0
|  | Labor Total |  |  | 2625 | 25% | 3500
|  | Inbound Freight, Expedite Fee, etc. |  |  | 175.175 |  | 175.175
|  | Material + Labor + Additional Totals |  |  | 20317.675 | 24.84% | 27031.8417
|  | Additional TAS Margin (if any) |  |  |  |  | 0
|  | Rep Commission (if any) |  |  |  |  | 0
|  | Sell Price |  |  |  |  | 27031.8417
|  | Total TAS Margin |  |  |  | 24.84%
|  | Total Margin |  |  |  | 24.84%
|  | Sub-Total (for quoting purposes) |  |  |  |  | 0
|  | Total - SubTotal |  |  |  |  | 27031.8417
Note on I9: Brad Byrum: Place "S" in row if you want this item included in the subtotal.

## UPS
Quote Title: (Use Customer Meaningful Title)
Company:
Requested by:
Contact Info:
Date: |  |  |  |  | Power
Created by: |  |  | AI = |  | DI= | [5 empty] | Buy/Resell
Peer Review by: |  |  | AO = |  | DO= | [5 empty] | Commission
Peer Review by: | [10 empty] | Direct
|  | Is this for Buy/Resell, Rep Commission or Direct? | Buy/Resell |  | Starting Margin = | 25% |  | S
Parts List Descriptions (for Formal Quote) | Vendor Name (or Stock)- (internal use) | Part Numbers (Internal Use) | Cost/ea. | Qty | Total Cost | 25.3 | Total Sell Price |  |  | Quote Description
[5 empty] | 0 | 25% | 0 |  | FALSE | Material: (Use Salesy terms and simplify by grouping like items (i.e., 20 Meter Cable Sets, not all the pieces))
[5 empty] | 0 | 25% | 0 |  | FALSE | -
PULS 24VDC, 20A Power Supply | PULS | CP20.241 | 276.45 | 1 | 276.45 | 25% | 368.6 |  | FALSE | -
PULS UPS Controller | PULS | UB40.241 | 555.75 | 1 | 555.75 | 25% | 741 |  | FALSE | -
[5 empty] | 0 | 25% | 0 |  | FALSE | -
10 amp AC Circuit Breaker | Reynolds | 1489-M1C100 | 18.39 | 1 | 18.39 | 25% | 24.52 |  | FALSE | -
20 amp DC Circuit Breaker | Reynolds | 1492-D1C200 | 26.14 | 1 | 26.14 | 25% | 34.8533 |  | FALSE | -
[5 empty] | 0 | 25% | 0 |  | FALSE | -
Phoenix Contact UT 6 Feed Thru Terminal Block | Graybar | 3044131 | 1.16 | 10 | 11.6 | 25% | 15.4667 |  | FALSE | -
Phoenix Contact UT 6 Feed Thru Ground Block | Graybar | 3044157 | 3.04 | 6 | 18.24 | 25% | 24.32 |  | FALSE | -
Phoenix Contact UT35 | Graybar | 3044225 | 3.86 | 3 | 11.58 | 25% | 15.44 |  | FALSE | -
Phoenix Contact End Blocks | Graybar | 0800886 | 0.97 | 2 | 1.94 | 25% | 2.5867 |  | FALSE | -
[5 empty] | 0 | 25% | 0 |  | FALSE | -
[5 empty] | 0 | 25% | 0
Ground Bars | Graybar | CHN125C | 16 | 1 | 16 | 25% | 21.3333
[5 empty] | 0 | 25% | 0
6 Battery Enclosure | RDA |  | 630 | 1 | 630 | 25% | 840
110 AH, 12VDC Lead Acid Battery | RDA |  | 180 | 2 | 360 | 25% | 480
Battery Cable/Wire |  |  | 100 | 1 | 100 | 25% | 133.3333
[5 empty] | 0 | 25% | 0 |  | FALSE | -
MISC |  |  | 150 | 1 | 150 | 25% | 200 |  | FALSE
[5 empty] | 0 | 25% | 0 |  | FALSE | Scope: (Record everything you told the customer it would do AND what you plan for it to do)
[5 empty] | 0 | 25% | 0 |  | FALSE
[5 empty] | 0 | 25% | 0 |  | FALSE
[5 empty] | 0 | 25% | 0 |  | FALSE
[5 empty] | 0 | 25% | 0
[5 empty] | 0 | 25% | 0
[5 empty] | 0 | 25% | 0
[5 empty] | 0 | 25% | 0
[5 empty] | 0 | 25% | 0
[5 empty] | 0 | 25% | 0
[5 empty] | 0 | 25% | 0
[5 empty] | 0 | 25% | 0
[5 empty] | 0 | 25% | 0
[5 empty] | 0 | 25% | 0
[5 empty] | 0 | 25% | 0
[5 empty] | 0 | 25% | 0
[5 empty] | 0 | 25% | 0
[5 empty] | 0 | 25% | 0
[5 empty] | 0 | 25% | 0
[5 empty] | 0 | 25% | 0
[5 empty] | 0 | 25% | 0
[5 empty] | 0 | 25% | 0
[5 empty] | 0 | 25% | 0
[5 empty] | 0 | 25% | 0
[5 empty] | 0 | 25% | 0
[5 empty] | 0 | 25% | 0
[5 empty] | 0 | 25% | 0
[5 empty] | 0 | 25% | 0
[5 empty] | 0 | 25% | 0
[5 empty] | 0 | 25% | 0
[5 empty] | 0 | 25% | 0 |  | FALSE
[5 empty] | 0 | 25% | 0 |  | FALSE
[5 empty] | 0 | 25% | 0 |  | FALSE
[5 empty] | 0 | 25% | 0 |  | FALSE
[5 empty] | 0 | 25% | 0 |  | FALSE
[5 empty] | 0 | 25% | 0 |  | FALSE
[5 empty] | 0 | 25% | 0 |  | FALSE
[5 empty] | 0 | 25% | 0 |  | FALSE
[5 empty] | 0 | 25% | 0 |  | FALSE
[5 empty] | 0 | 25% | 0 |  | FALSE
|  | Material Total |  |  | 2176.09 | 25% | 2901.4533 |  | 0
|  | Shop Labor Cost | 52.5 | 8 | 420 | 25% | 560
|  | Engineering and Programming Labor Cost | 70 | 0 | 0 | 25% | 0
|  | Labor Total |  |  | 420 | 25% | 560
|  | Inbound Freight, Expedite Fee, etc. |  |  | 50 |  | 50
|  | Material + Labor + Additional Totals |  |  | 2646.09 | 24.64% | 3511.4533
|  | Additional TAS Margin (if any) |  |  |  |  | 0
|  | Rep Commission (if any) |  |  |  |  | 0
|  | Sell Price |  |  |  |  | 3511.4533
|  | Total TAS Margin |  |  |  | 24.64%
|  | Total Margin |  |  |  | 24.64%
|  | Sub-Total (for quoting purposes) |  |  |  |  | 0
|  | Total - SubTotal |  |  |  |  | 3511.4533
Note on I9: Brad Byrum: Place "S" in row if you want this item included in the subtotal.

## Labor Estimate
Quote Title (Use Customer Meaningful Title): | #REF!
Customer Name: | #REF!
Requested by: | #REF!
Contact Info: | #REF!
Date: | #REF!
Created by: | #REF! | [6 empty] | Buy/Resell
Peer Review by: | #REF! | [6 empty] | Commission
Peer Review by: | #REF! | [6 empty] | Direct
Work Order Number: | #REF!
| Item/Category | Assigned To | Charge Rate | Qty/Hours | Total Sell Price
Project Engineering (Remote Work)
| Project Management |  |  |  | 0
| Design |  | 130 |  | 0
| Drawing |  | 130 |  | 0
| Programming |  | 160 |  | 0
| Factory Acceptance Test Labor |  |  |  | 0
| Non-Reoccuring Engineering Fee |  |  |  | 0
| Troubleshooting |  |  |  | 0
Field Service (Site Work)
| Project Management |  | 160 |  | 0
| Programming |  |  |  | 0
| Commissioning |  | 160 |  | 0
| Troubleshooting |  |  |  | 0
| Site Survey |  |  |  | 0
| Travel Time |  |  |  | 0
| Travel Rate |  |  |  | 0
| Per Diem |  | 125 |  | 0
| Truck Charge |  | 30 |  | 0
[6 empty] | Sub-Contract Cost | Sub-Contract Margin
| Subcontractor Labor |  |  |  | 0
| Total Labor |  |  |  | 0

## Additional List
Margin
0%
5%
8%
10%
12%
15%
17.2%
19.6%
22%
24.4%
25%
26.8%
29.2%
31.6%
34%
36.4%
38.8%
41.2%
43.6%
46%
48.4%
50%
50.8%

## Data List
LIT | LIT
Column1 | Tag | PID | MFG | P/N | QTY | Equipment | Description | Column5 | AI | AI Signal Use | AO | AO Signal Use | DI | DI Signal Use | DO | DO Signal Use | MB | MB Signal Use
| LIT-007 | PID-1000 | Magnetrol | 706-540A-310 | 1 | Tank Level | ECLIPSE 4th Generation Guided Wave Radar |  | 1 | Tank Level
| LIT-008 | PID-1000 | Magnetrol | 706-540A-310 | 1 | Tank Level | ECLIPSE 4th Generation Guided Wave Radar |  | 1 | Tank Level
| LIT-021 | PID-1000 | Magnetrol | 706-540A-310 | 1 | Tank Level | ECLIPSE 4th Generation Guided Wave Radar |  | 1 | Tank Level
| LIT-030 | PID-1000 | Magnetrol | 706-540A-310 | 1 | Tank Level | ECLIPSE 4th Generation Guided Wave Radar |  | 1 | Tank Level
| LIT-031 | PID-1000 | Magnetrol | 706-540A-310 | 1 | Tank Level | ECLIPSE 4th Generation Guided Wave Radar |  | 1 | Tank Level
| LIT-013 | PID-1001 | Magnetrol | 706-540A-310 | 1 | Tank Level | ECLIPSE 4th Generation Guided Wave Radar |  | 1 | Tank Level
| LIT-013 | PID-1000 | Magnetrol | 706-540A-309 | 1 | Tank Level | ECLIPSE 4th Generation Guided Wave Radar |  | 1 | Tank Level
|  |  |  | Total Devices Required | 7 |  |  | Total AI | 7
Flowmeter | FIT
Column1 | Tag | PID | MFG | P/N | QTY | Equipment | Column4 | Column5 | AI | AI Signal Use | AO | AO Signal Use | DI | DI Signal Use | DO | DO Signal Use | MB | MB Signal Use
| FIT-700 | PID-1000 | Yokogawa | AXG150-CASF2BA1AL212B-2M011/GRL/MC | 1 | Comstock Line | [10 empty] | 1 | Comstock PipeLine Flow Meter
| FIT-600 | PID-1001 | Yokogawa | AXG150-CASF2BA1AL212B-2M011/GRL/MC | 1 | Well #1 Injection Run Suction Header | [10 empty] | 1 | P-601/602 Suction Header
| FIT-601 | PID-1001 | Yokogawa | AXG150-CASF2BA1AL212B-2M011/GRL/MC | 1 | Well #1 Injection to well | [10 empty] | 1 | P-601/602 Discharge Header
| FIT-700 | PID-1001 | Yokogawa | AXG150-CASF2BA1AL212B-2M011/GRL/MC | 1 | Well #2 Injection to well | [10 empty] | 1 | Injection Well #2 Flowmeter
|  |  |  | Total In Use | 4 |  |  | Total AI
LSH | LSH
Column1 | Tag | PID | MFG | P/N | QTY | Equipment | Column4 | Column5 | AI | AI Signal Use | AO | AO Signal Use | DI | DI Signal Use | DO | DO Signal Use | MB | MB Signal Use
| LSH-001 | PID-1000 | Magnetrol | 961-2DA1-030 w/ 9A1-A21A-012 | 1 | Buffer Tank TK-001 | Echotel Model 961 Ultrasonic Level Switch | [5 empty] | 1 | HH Level Buffer Tank TK-001
| LSH-002 | PID-1000 | Magnetrol | 961-2DA1-030 w/ 9A1-A21A-012 | 1 | Buffer Tank TK-002 | Echotel Model 961 Ultrasonic Level Switch | [5 empty] | 1 | HH Level Buffer Tank TK-002
| LSH-003 | PID-1000 | Magnetrol | 961-2DA1-030 w/ 9A1-A21A-012 | 1 | Buffer Tank TK-003 | Echotel Model 961 Ultrasonic Level Switch | [5 empty] | 1 | HH Level Buffer Tank TK-003
| LSH-004 | PID-1000 | Magnetrol | 961-2DA1-030 w/ 9A1-A21A-012 | 1 | Buffer Tank TK-004 | Echotel Model 961 Ultrasonic Level Switch | [5 empty] | 1 | HH Level Buffer Tank TK-004
| LSH-005 | PID-1000 | Magnetrol | 961-2DA1-030 w/ 9A1-A21A-012 | 1 | Buffer Tank TK-005 | Echotel Model 961 Ultrasonic Level Switch | [5 empty] | 1 | HH Level Buffer Tank TK-005
| LSH-006 | PID-1000 | Magnetrol | 961-2DA1-030 w/ 9A1-A21A-012 | 1 | Buffer Tank TK-006 | Echotel Model 961 Ultrasonic Level Switch | [5 empty] | 1 | HH Level Buffer Tank TK-006
| LSH-007 | PID-1000 | Magnetrol | 961-2DA1-030 w/ 9A1-A21A-012 | 1 | Buffer Tank TK-007 | Echotel Model 961 Ultrasonic Level Switch | [5 empty] | 1 | HH Level Buffer Tank TK-007
| LSH-008 | PID-1000 | Magnetrol | 961-2DA1-030 w/ 9A1-A21A-012 | 1 | Buffer Tank TK-008 | Echotel Model 961 Ultrasonic Level Switch | [5 empty] | 1 | HH Level Buffer Tank TK-008
| LSH-009 | PID-1001 | Magnetrol | 961-2DA1-030 w/ 9A1-A21A-012 | 1 | Clean Tank TK-009 | Echotel Model 961 Ultrasonic Level Switch | [5 empty] | 1 | HH Level Clean Tank TK-009
| LSH-010 | PID-1001 | Magnetrol | 961-2DA1-030 w/ 9A1-A21A-012 | 1 | Clean Tank TK-010 | Echotel Model 961 Ultrasonic Level Switch | [5 empty] | 1 | HH Level Clean Tank TK-010
| LSH-011 | PID-1001 | Magnetrol | 961-2DA1-030 w/ 9A1-A21A-012 | 1 | Clean Tank TK-011 (Existing) | Echotel Model 961 Ultrasonic Level Switch | [5 empty] | 1 | HH Level Clean Tank TK-011 (Existing)
| LSH-012 | PID-1001 | Magnetrol | 961-2DA1-030 w/ 9A1-A21A-012 | 1 | Clean Tank TK-012 (Existing) | Echotel Model 961 Ultrasonic Level Switch | [5 empty] | 1 | HH Level Clean Tank TK-012 (Existing)
| LSH-013 | PID-1001 | Magnetrol | 961-2DA1-030 w/ 9A1-A21A-012 | 1 | Clean Tank TK-013 (Existing) | Echotel Model 961 Ultrasonic Level Switch | [5 empty] | 1 | HH Level Clean Tank TK-013 (Existing)
| LSH-014 | PID-1001 | Magnetrol | 961-2DA1-030 w/ 9A1-A21A-012 | 1 | Clean Tank TK-014 (Existing) | Echotel Model 961 Ultrasonic Level Switch | [5 empty] | 1 | HH Level Clean Tank TK-014 (Existing)
| LSH-020 | PID-1000 | Magnetrol | 961-2DA1-030 w/ 9A1-A21A-012 | 1 | Oil Tank TK-020 | Echotel Model 961 Ultrasonic Level Switch | [5 empty] | 1 | HH Level Oil Tank TK-020
| LSH-021 | PID-1000 | Magnetrol | 961-2DA1-030 w/ 9A1-A21A-012 | 1 | Oil Tank TK-021 | Echotel Model 961 Ultrasonic Level Switch | [5 empty] | 1 | HH Level Oil Tank TK-021
| LSH-030 | PID-1000 | Magnetrol | 961-2DA1-030 w/ 9A1-A21A-012 | 1 | Gun Barrel TK-030 | Echotel Model 961 Ultrasonic Level Switch | [5 empty] | 1 | HH Level Gun Barrel TK-030
| LSH-031 | PID-1000 | Magnetrol | 961-2DA1-030 w/ 9A1-A21A-012 | 1 | Gun Barrel TK-031 | Echotel Model 961 Ultrasonic Level Switch | [5 empty] | 1 | HH Level Gun Barrel TK-031
|  |  |  | Total in Use | 18 |  |  | Total AI
[12 empty] | Total | 18
PIT #1 | PIT #1
Column1 | Tag | PID | MFG | P/N | QTY | Equipment | Column4 | Column5 | AI | AI Signal Use | AO | AO Signal Use | DI | DI Signal Use | DO | DO Signal Use | MB | MB Signal Use
| PIT-601 | PID-1001 | Yokogawa | EJA530E-JBS7N-012EL/FU1/D1 | 1 | Well #1 Injection Run Filter #1 (F-600 prefilter) In uses as DP | Low |  | 1
| PIT-602 | PID-1001 | Yokogawa | EJA530E-JBS7N-012EL/FU1/D1 | 1 | Well #1 Injection Run Filter #1 (F-600 Post Filter) In uses as DP | Low |  | 1
| PIT-607 | PID-1001 | Yokogawa | EJA530E-JBS7N-012EL/FU1/D1 | 1 | Well #1 Injection Run Filter #2 (F-601 prefilter) In uses as DP | Low |  | 1
| PIT-608 | PID-1001 | Yokogawa | EJA530E-JBS7N-012EL/FU1/D1 | 1 | Well #1 Injection Run Filter #2 (F-601 postfilter) In uses as DP | Low |  | 1
| PIT-621 | PID-1001 | Yokogawa | EJA530E-JBS7N-012EL/FU1/D1 | 1 | Well #1 Injection Run Suction Header (Wellhead #1 Injection pump header) | Low |  | 1
| PIT-701 | PID-1001 | Yokogawa | EJA530E-JBS7N-012EL/FU1/D1 | 1 | Well #2 Injection Run 1 Filter (F-701 prefilter) In uses as DP | Low |  | 1
| PIT-703 | PID-1001 | Yokogawa | EJA530E-JBS7N-012EL/FU1/D1 | 1 | Well #2 Injection Run 1 Filter (F-701 postfilter) In uses as DP | Low |  | 1
| PIT-713 | PID-1001 | Yokogawa | EJA530E-JBS7N-012EL/FU1/D1 | 1 | Well #2 Injection Run 2 Filter (F-702 prefilter) In uses as DP | Low |  | 1
| PIT-715 | PID-1001 | Yokogawa | EJA530E-JBS7N-012EL/FU1/D1 | 1 | Well #2 Injection Run 2 Filter (F-702 postfilter) In uses as DP | Low |  | 1
| PIT-725 | PID-1001 | Yokogawa | EJA530E-JBS7N-012EL/FU1/D1 | 1 | Well #2 Injection Run 3 Filter (F-704 prefilter) In uses as DP | Low |  | 1
| PIT-727 | PID-1001 | Yokogawa | EJA530E-JBS7N-012EL/FU1/D1 | 1 | Well #2 Injection Run 3 Filter (F-704 postfilter) In uses as DP | Low |  | 1
| PIT-737 | PID-1001 | Yokogawa | EJA530E-JBS7N-012EL/FU1/D1 | 1 | Well #2 Injection Run 4 Filter (F-706 prefilter) In uses as DP | Low |  | 1
| PIT-739 | PID-1001 | Yokogawa | EJA530E-JBS7N-012EL/FU1/D1 | 1 | Well #2 Injection Run 4 Filter (F-706 postfilter) In uses as DP | Low |  | 1
|  |  |  | Total in Use | 13 |  |  | Total AI
PIT #2 | PIT #2
Column1 | Tag | PID | MFG | P/N | QTY | Equipment | Column4 | Column5 | AI | AI Signal Use | AO | AO Signal Use | DI | DI Signal Use | DO | DO Signal Use | MB | MB Signal Use
| PIT-619 | PID-1001 | Yokogawa | EJA530E-JDS7N-012EL/FU1/D1 | 1 | Well #1 Injection Run 1 (P-601 Discharge PSI) | High
| PIT-629 | PID-1001 | Yokogawa | EJA530E-JDS7N-012EL/FU1/D1 | 1 | Well #1 Injection Run 2 (P-602 Discharge PSI) | High
| PIT-633 | PID-1001 | Yokogawa | EJA530E-JDS7N-012EL/FU1/D1 | 1 | Well #1 Injection to well (Injection PSI) | High
| PIT-634 | PID-1001 | Yokogawa | EJA530E-JDS7N-012EL/FU1/D1 | 1 | Well #1 Injection to well ( Anulus) | High
| PIT-710 | PID-1001 | Yokogawa | EJA530E-JDS7N-012EL/FU1/D1 | 1 | Well #2 Injection Run 1 (P-701 Discharge PSI) | High
| PIT-722 | PID-1001 | Yokogawa | EJA530E-JDS7N-012EL/FU1/D1 | 1 | Well #2 Injection Run 2 (P-703 Discharge PSI) | High
| PIT-734 | PID-1001 | Yokogawa | EJA530E-JDS7N-012EL/FU1/D1 | 1 | Well #2 Injection Run 3 (P-705 Discharge PSI) | High
| PIT-746 | PID-1001 | Yokogawa | EJA530E-JDS7N-012EL/FU1/D1 | 1 | Well #2 Injection Run 4 Filter (P-706 Discharge PSI) | High
| PIT-750 | PID-1001 | Yokogawa | EJA530E-JDS7N-012EL/FU1/D1 | 1 | Well #2 Injection to well (Injection PSI) | High
| PIT-751 | PID-1001 | Yokogawa | EJA530E-JDS7N-012EL/FU1/D1 | 1 | Well #2 Injection to well (Anulus PS) | High
|  |  |  | Total in Use | 10 |  |  | Total AI
MOV | MOV
Column1 | Tag | PID | MFG | P/N | QTY | Equipment | Column4 | Column5 | AI | AI Signal Use | AO | AO Signal Use | DI | DI Signal Use | DO | DO Signal Use | MB | MB Signal Use
0
|  |  |  | Total in Use | 0 |  |  | Total AI
Device Name Here
| Column1 | Tag | PID | MFG | P/N | QTY | Equipment | Column4 | AI | AI Signal Use | AO | AO Signal Use | DI | DI Signal Use | DO | DO Signal Use | MB | MB Signal Use
0
[5 empty] | Total in Use | 0 |  | Total AI
Device Name Here
| Column1 | Tag | PID | MFG | P/N | QTY | Equipment | Column4 | AI | AI Signal Use | AO | AO Signal Use | DI | DI Signal Use | DO | DO Signal Use | MB | MB Signal Use
0
[5 empty] | Total in Use | 0 |  | Total AI
| Column1 | Tag | PID | MFG | P/N | QTY | Equipment | Column4 | AI | AI Signal Use | AO | AO Signal Use | DI | DI Signal Use | DO | DO Signal Use | MB | MB Signal Use
0
[5 empty] | Total in Use | 0 |  | Total AI

## Sheet2 (hidden)
Device Name Here
Column1 | Tag | PID | MFG | P/N | QTY | Equipment | Column4 | Column5 | Column6 | Column7 | Column8
0
|  |  |  | Total in Use | 0
Device Name Here
Column1 | Tag | PID | MFG | P/N | QTY | Equipment | Column4 | Column5 | Column6 | Column7 | Column8
0
|  |  |  | Total in Use | 0